## Slide 1
Module 10:
Energy efficiency in lighting systems
TRAINING PROGRAMME
for MANAGEMENT OFFICERS
This Module provides very good information on lighting. There are many suggestions provided to improve it. In particular, the examples and much of the discussion should focus on industrial lighting applications.
Other minor comments included.

## Slide 2: CONTENTS
Lighting system parameters
Selection of lighting equipment
Energy-efficient and effective lighting systems

## Slide 3
I. Lighting system parameters

## Slide 4: CONCEPT
Luminous flux is the measure of the power of light emitted by a light source, expressed in Lumens (lm). The luminous flux for 1 watt at a wavelength (within the optical range) of 555 nm is 683 lm. The human eye perceives differently at different wavelengths. The visible spectrum of human vision ranges from 380 nm to 780 nm.

## Slide 5: CONCEPT
Luminous intensity is the luminous flux emitted in a particular direction within a solid angle Ω. The unit of measure for luminous intensity is the candela (cd). Candela is the fundamental unit in lighting technology, from which all other units are derived. 1 candela indicates that a light source emits 1 lumen per steradian in a specific direction.

## Slide 6: CONCEPT
Illuminance is the density of luminous flux on a unit area dS of a surface being illuminated, measured in lux (lx). Illuminance assesses the density of luminous flux, indicating the amount of luminous flux from a light source incident on a specific area. Illuminance decreases inversely with the square of the distance from the light source (inverse-square law).
Distance
1 m2 Surface area of a sphere
Light intensity
Radius
Luminous flux

## Slide 7: CONCEPT
Average illuminance is defined as the luminous flux Φ incident on a surface area A.
Illuminance at a point is calculated using the luminous intensity (I) and the difference (a) between the light source and the given point

## Slide 8: CONCEPT
Luminous efficacy is calculated as the ratio of luminous flux to electrical power consumption of the lamp, defined as lumens per watt (lm/W).

## Slide 9: LIGHT QUALITY
Factors that indicate light quality
1. Glare
2. Uniformity
3. Color rendering index
4. Light color or color temperature

## Slide 10: 1. Glare
The glare of a lit surface is the ratio of luminous intensity to the area of the illuminated surface
Light can be reflected by a surface or transmitted through it. Glare serves as the basis for describing the perceived brightness level; in reality, brightness is influenced by eye adaptation, the reflectance ratio, or the absorption of the surface.

## Slide 11: 2. Uniformity
Uniformity characterizes the evenness of illuminance across different areas.
For example:
  In a factory:
    20% of the area may require 300 lux of illumination, while the remaining 80% may only need 200 lux.
    However, when designing the lighting, uniform illumination of the entire factory at 300 lux is implemented. This results in significant energy and cost wastage.
    At the desk:
    Uneven lighting => uneven brightness on the desk surface => causing discomfort for the workers.

## Slide 12: 3. Color Rendering Index
The Color Rendering Index (CRI), represented as Ra, indicates the color accuracy of an object when illuminated by a light source.
Sunlight has a CRI of Ra = 100. High-pressure sodium streetlights have a CRI of Ra = 26, while fluorescent lights typically have a CRI > 70. A low CRI indicates color distortion of objects illuminated by that light source.

## Slide 13: 4. Color temperature
Yellow light creates a warm atmosphere.
White light creates a cool atmosphere.
Blue light is very close to natural daylight.
The color temperature of a light bulb is the temperature of a black body radiator at which it emits light of the same color as the light emitted by the bulb.

## Slide 14: 4. Color temperature
The color of light is expressed through color temperature, measured in degrees Kelvin (K).
        Warm light < 3000K Neutral white light = 3000 – 5000K Cool white light > 5000K

## Slide 15: Determining the color temperature
The Kruithof diagram
Degree

## Slide 16: Determining the Color Rendering Index (CRI)
Group | Ra | Field of application
1A | Ra ≥ 90 | Excellent, places where color rendition is crucial are paramount.
1B | 80 ≤ Ra < 90 | Great, used in places where accurate color reproduction is essential.
2 | 60 ≤ Ra < 80 | Medium, used in places where moderate color representation is sufficient.
3 | 40 ≤ Ra < 60 | Low, used in places where there is no requirement for color rendition.
4 | 20 ≤ Ra < 40 | Very low, the colors of objects are completely distorted.

## Slide 17: Standards for illuminance and glare
TCVN 7114: 2008

## Slide 18: Standards for illuminance and glare
QCVN 09:2017/BXD
Functional Area | Illuminance Range (lux) | Recommended LPD (W/m²)
Rough processing / Warehousing / Semi-finished goods | 100 - 300 | 6 - 9
Light mechanical assembly | 300 – 500 | 9 - 12
Precision machining, product inspection | 500 - 750 | 11 - 15
Cold storage, packaging area | 100 - 200 | 4 - 7
Maintenance, technical repair workshop | 300 – 500 | 8 - 11
Production areas with high lighting requirements | ≥1000 | 14 - 18

## Slide 19: Causes of ineffective lighting systems
Selecting specifications that do not meet standards or suit usage needs.
Choosing inappropriate lighting equipment.
Improper arrangement of lighting fixtures.
Interference from other equipment in the lighting area.
Ineffective maintenance.
Lack of energy-saving awareness.

## Slide 20
II. SELECTION OF LIGHTING EQUIPMENT

## Slide 21: Types of lighting lamps
Filament lamp
Halogen
Fluorescent lamp (FL)
Compact Fluorescent lamp (CFL)
Low pressure sodium (LPS)
Metal Halide
High pressure sodium
High pressure mercury
LED
Induction
LED used in industry

## Slide 22: Comparing luminous efficiency
Luminous efficiency
Halogen
Filament
Fluorescent
HQ Compact 5-26W
Metal Halide
HQ Compact >26W
Low-pressure sodium
High-pressure sodium
High-pressure mercury
LED
Sensor

## Slide 23: Comparing lighting quality

## Slide 24: AUXILIARY DEVICES IN LIGHTING SYSTEMS
Lamp Replector
Magnetic Ballast
Lamp Replector
Starter
LED Driver

## Slide 25: Ballast
A device that limits current to reduce the negative resistance of discharge lamps. For fluorescent lamps, this device helps accumulate the initial voltage needed to turn on the lamp
Magnetic Ballast
(Preheat start)
Advantages:
  Cheap
Disavantages:
  High energy consumption,
  Noisy and hot
  Long ignition time -> reducing bulb lifespan

## Slide 26: Ballast
Electronic Ballast
Advantages:
  Reduces energy consumption by 20-40%
  Increases bulb lifespan by 30-50%
  Increases bulb lifespan by 30-50%
  Enhances light emission efficiency by 30-50%
Disadvantages:
  High cost

## Slide 27: Reflective Surface (Lamp Reflector)
The reflectivity of materials and the shape of the reflective surface directly impact the efficiency and performance of lighting installations.
Typically, new diffuse reflectors have a reflectance efficiency of 70-80%.
Newer high-reflectivity or semi-diffuse materials can achieve a reflectance rate of up to 85%.

## Slide 28: Choosing light reflectors
1. Choosing light reflectors – factory area

## Slide 29: Choosing light reflectors
2. Choosing light reflectors – office, civil

## Slide 30: Visual comfort

## Slide 31: What defines an efficient lighting system?
Ensure visual comfort
Reduce energy consumption
Discussion

## Slide 32: Choosing light bulbs
Field of application
Luminous efficacy
Color of light, color rendering index (CRI)
Lifespan
Wattage of the bulb, warm-up time
Luminous flux depreciation
Dimming capability

## Slide 33: Common errors in lamp usage
Focusing solely on initial cost of light bulbs
Inaccurate color rendition
Not suitable for the intended users
Choosing wattage that is too high or too low
Using inefficient magnetic ballasts
Frequent switching on and off

## Slide 34: CHOOSING LIGHT SOURCES
Type of light currently in use | Replaceable light | % saving | Application
Incandescent light | LED | 75-80% | Commercial, residential, restaurant, hotel
High-pressure mercury lamp | LED | 30-60% | Factory, trading area, sports facilities, supermarket
High-pressure mercury lamp | LED | 40-50% | Public spaces, streets, outdoors
Fluorescent lamp – T10 | LED | 10-50% | Industrial, residential, public...
Small incandescent indicator light for electrical panels | LED | 70% | Electrical panels, transportation
Halogen | CFL, LED | 60-65% | Decoration, hotels, convenience stores

## Slide 35
III. ENERGY-EFFICIENT AND EFFECTIVE LIGHTING SYSTEMS

## Slide 36: UTILIZING NATURAL LIGHT
Natural light is free and beneficial for health. Therefore, maximizing the use of natural light and reducing the use of electric lights is a highly effective energy-saving potential that should be considered from the design phase onward.
Properly design windows, skylights, and light wells.
Use light tubes to bring light from the roof deep into the building, especially in areas that do not receive direct natural light from windows and skylights.

## Slide 37: UTILIZING NATURAL LIGHT

## Slide 38: UTILIZING NATURAL LIGHT
Case Study
Application point: Evaluate the use of natural daylight during the day by applying light-transmitting materials to areas within the factory that do not receive natural light.
Analysis and measurement method:
  Determine if the factory ceiling can be replaced with materials that allow direct sunlight onto the roof.
  Assess the current status of lighting fixtures that are on due to lack of natural light usage.
  To calculate the efficiency of energy savings, determine the power rating, quantity installed, number of fixtures, and lighting duration of the lighting devices under natural sunlight in the applicable area.

## Slide 39: UTILIZING NATURAL LIGHT
Before Renovation
SOLUTION:
Install internal shading panels
Create ventilation openings
After Renovation

## Slide 40: UTILIZING NATURAL LIGHT

## Slide 41: UTILIZING NATURAL LIGHT
Case study
Preventive Measures for Improvement:
  It is necessary to determine beforehand whether natural light affects product quality within the factory.
  Propose regular maintenance and inspections to prevent reduced natural light due to solar light pollution
Energy Saving Efficiency:
  Daily electricity savings = [Total electrical energy consumption (W) of lights turned on during daytime in areas with sunlight] x [Average daily natural light exposure time (h/d)]

## Slide 42: Replacing light bulbs with high-efficiency bulbs
Incandescent lamp
fluorescent lamp
Compact fluorescent lamp
LED lamp
Luminous efficacy(lm/W)
Replacing light bulbs to improve lighting efficiency is a straightforward method to save energy. Effective replacement light sources should be chosen to ensure they are both energy-efficient and suitable without compromising lighting quality.

## Slide 43: Replacing light bulbs with high-efficiency bulbs
Research Case: Replacing Low-Efficiency Bulbs with LED Lights
Application Point: Incandescent and halogen bulbs are prime examples of low-efficiency lighting devices. We are considering replacing them with LED lights, which are high-efficiency lighting devices.
Analysis and Measurement Method: To calculate the savings efficiency, determine the power consumption of incandescent and halogen bulbs, the quantity installed, the number of lights, and the annual lighting duration.

## Slide 44: Replacing light bulbs with high-efficiency bulbs
Research Case: Replacing Low-Efficiency Bulbs with LED Lights
Improvement Directions:
  30 W incandescent bulbs → 4-5 W LED bulbs.
  60 W incandescent bulbs → 8-10 W LED bulbs.
  100 W incandescent bulbs → 15-20 W LED bulbs.
Energy saving efficiency
Electricity savings per unit = [Power consumption of incandescent and halogen bulbs (W)] - [Power consumption of LED bulbs (W)]
Incandescent bulbs and halogen bulbs
LED bulbs

## Slide 45: Replacing light bulbs with high-efficiency bulbs
Example: Replacing Lighting System for a Production workshop.
A production workshop is currently using 415 fluorescent T8 tubes to illuminate its aisle spaces. Replacing all these T8 tubes with LED tubes (of equivalent luminous flux) would save energy for the production workshop.

## Slide 46: Replacing light bulbs with high-efficiency bulbs
Thông số | Unit | Fluorescent lamp T8 | LED 18W
Power of bulbs | W | 36 | 18
Ballast power | W | 8 | 0
Total power consumption of a set of bulbs | W | 44 | 18
Number of bulbs | Bulb | 415 | 415
Simultaneous use factor | % | 80% | 80%
Cost of bulbs, materials, and installation | VND | – | 165.000
Average daily operation | Hour | 8 | 8
Number of operating days in a year | Day | 260 | 260
Number of operating hours in a year | Hour | 2.080 | 2.080
Electricity consumption | kWh | 24.860 | 12.430
Annual electricity savings | kWh |  | 12.430
Average electricity price | VNĐ /kWh | 2.371 | 2.371
Annual electricity cost | VND | 58.943.439 | 29.471.720
Annual electricity cost savings | VND |  | 29.471.720
Total investment cost | VND |  | 68.475.000
Net Present Value (NPV) (over 5 years, discounted at 12% per year) | VND |  | 37.763.955
Payback period | Year |  | 2,9
Internal Rate of Return (IRR) | % |  | 32,6

## Slide 47: Minimizing unnecessary lighting
Lighting Control Circuit Layout

## Slide 48: Minimizing unnecessary lighting
Timer
Motion sensor
Light sensor
360-degree multi-function sensor
Using automatic lighting control system

## Slide 49: Minimizing unnecessary lighting
Research Case: Using Motion Sensors
Application Point:
  Considered for controlling lighting in areas without people, such as restrooms, staircases, hallways, etc., where lighting may not be necessary.
  Considered for turning on lighting devices even in unnecessary areas during daytime when natural light is sufficient.
Analysis and Measurement Method:
  Identify lighting fixtures or areas where lights are turned on unnecessarily when no one is present.
  Identify lighting fixtures or areas that are turned on unnecessarily during the day due to natural light.
  To calculate energy efficiency, determine the power consumption, the number of installations, lighting levels, and the unnecessary lighting duration of lighting fixtures in the applicable area.

## Slide 50: Minimizing unnecessary lighting
Research Case: Using Motion Sensors
Energy Saving Efficiency
  Electricity savings = [Total electricity consumption (Wh) for lighting] x [Percentage of time that can be turned off by motion sensor detection during lighting time (%) / 100]
Human presence sensor using infrared detection
Principle and RF body detection sensor

## Slide 51: Minimizing unnecessary lighting
Research Case: Using Motion Sensors
Preventive Measures for Improvement:
  In areas with high foot traffic, such as restrooms, frequent switching on and off of lighting fixtures due to multiple users can potentially shorten the lifespan of the lighting equipment, so this aspect needs careful consideration.
  Body motion sensors must be configured to control multiple lighting fixtures.

## Slide 52: Minimizing unnecessary lighting
Automatically turning off lights when sufficient light levels are reached

## Slide 53: Using Electronic Ballasts
Electronic ballasts are commonly used to provide a higher voltage to start fluorescent tubes and then limit the current during operation. The losses in electronic ballasts for fluorescent tubes are around 2-3 W, compared to 10-15 W when using standard magnetic ballasts.
Type | Power consumption of the bulbs: |  | Power saving(W)
 | Magnetic ballast (W) | Electronic ballast (W) | 
Fluorescent tube 36W | 45 | 38 | 7
High-pressure Sodium lamp 70W | 81 | 75 | 6

## Slide 54: AREA-SPECIFIC LIGHTING
Area-specific lighting involves providing optimal illumination tailored to the specific work area, focusing directly on the actual working space.
In contrast, general lighting for workshops or offices is maintained at a lower level."

## Slide 55: Optimizing Lighting
Case study:
Application Point: Maintaining appropriate lighting levels by reducing light output when using excessive lighting fixtures in the illuminated area.
Analysis and Measurement Method:
  Measure brightness levels
  Improvements are considered based on the illumination levels between the lighting fixtures.
  To calculate energy efficiency, determine the power consumption, number of installations, lighting levels, and unnecessary lighting duration of lighting fixtures in the illuminated area.
  Identify separate lighting circuits with switches.

## Slide 56: Optimizing Lighting
Example: sequential lights turning off in an underground parking lot
Smart lighting device
Case study:
Energy Saving Efficiency: Calculated based on electricity consumption and downtime.

## Slide 57: DESIGNING AN OPTIMAL LIGHTING SYSTEM
Some lighting standards
Specifications of common types of lights
Steps in lighting design

## Slide 58: Steps in lighting design
Step 1: Determine the mounting height of the lights.
h is the height of the workshop;
h1 is the distance from the ceiling to the light bulb, typically h1 = 0.5 - 0.7 meters;
h2 is the height of the working surface, typically h2 = 0.7 - 0.9 meters.

## Slide 59: Steps in lighting design
Step 2:
Determine the distance between two adjacent lights (L, m) according to the optimal L/H ratio.
Types of Lights and Their Applications | L/H multiple row arrangement |  | L/H single row arrangement |  | The limited width of the factory layout for a single row
 | Optimal | Maximum | Optimal | Maximum | 
Factory lighting using universal reflectors.r enamel-coated reflectors | 2,3 | 3,2 | 1,9 | 2,5 | 1,3H
Factory lighting using universal reflectors. | 1,8 | 2,5 | 1,8 | 2,0 | 1,2H
Office lighting | 1,6 | 1,8 | 1,5 | 1,8 | 1,0H

## Slide 60: Steps in lighting design
 | ceiling | wall | floor
Air-conditioned room | 0.7 | 0.5 | 0.2
Light industry | 0.5 | 0.3 | 0.1
Heavy industry | 0.3 | 0.2 | 0.1
Step 3:
The typical reflectance values used for parameters L5, L6, L7:

## Slide 61: Steps in lighting design
Step 4:
Calculate the index for a room size of a x b:
Step 5: find the utilization factor (KSD) using the reflectance coefficients and the φ table:
- The utilization factor is determined as a percentage of the lumens emitted by the ceiling light source and transmitted to the working surface
- This factor includes both direct light emitted from the light source as well as light reflected off the room surfaces
- Manufacturers provide a specific table derived from photometric test reports for each lighting fixture
- For twin-tube fluorescent lamps, the utilization factor is 0.66, corresponding to a room index of 2.5

## Slide 62: Steps in lighting design
Step 6: Determine the luminous flux of the bulb
k is the reserve factor.
E is the illuminance required by the factory (lx); S is the area of the factory (m2);
Z is the calculation factor, typically Z = 0.8 – 1.4;
n is the number of bulbs determined precisely after arranging the lights on the ground.
Environmental properties | Minimum times to clean the bulb/month. | Reserve factor | 
 |  | Fluorescent tube | Incandescent bulb
Heavy smoke, soot, fume | 4 | 2 | 1,7
Moderate smoke, soot, fume | 3 | 1,8 | 1,5
Light smoke, soot, fume | 2 | 1,5 | 1,3

## Slide 63: Steps in lighting design
Step 7: Refer to the handbook to find a bulb with luminous flux greater than or equal to the calculated luminous flux from step 6..
Step 8: Draw the lighting power distribution diagram on the ground.
Step 9: Draw the principle diagram for supplying electricity to the lighting..
Step 10: Select the elements on the principle diagram.

## Slide 64: Maintenance of the lighting system
Regularly clean lamps, reflectors, and reflective surfaces.
Replace faulty and soon-to-fail bulbs.
Replace protective lenses when yellowed.
Replace groups of lights when light levels decrease by more than 20-30%.
Lamps and reflectors covered in dust → reduce light output by 50%.

## Slide 65: CONCLUSION
For an energy-efficient lighting system:
Choose an appropriate number of lights.
Determine suitable light quality.
Utilize natural light.
Design logically according to needs.
Regularly audit and assess.
Maintain and upkeep.
Select the most efficient lighting technology

## Slide 66: QUIZ

## Slide 67: QUIZ

## Slide 68: QUIZ

## Slide 69
Thank you!