## Slide 1: TRAINING PROGRAME for IEs
The Vietnam Scaling up Energy Efficiency Project (VSUEE)
for: Enterprise leaders

## Slide 2: Training program for business leaders
TIME | Content
8.00 – 8.30 | Registration
8.30 – 8.40 | Opening Remarks
8.40 – 9.45 | Module 1: Project introduction Policy introduction: energy saving, greenhouse gas emission reduction, gender issues related in EE
9.45 – 10.00 | Breaks
10.00– 11.00 | Module 2. Relations between energy, environment and production and business, use of clean energy
11.00 – 11.45 | Module 3. The current situation of energy use and potential of industrial waste in Vietnam (cement, steel, seafood processing, brick and ceramic, textiles, beverages, paper and pulp, other industries (plastics...)
11.45 – 12.00 | Discuss
12.00 – 13.30 | Lunch
13.30 – 14.15 | Module 4. Energy Management, Energy Management System
14.15 – 15.00 | Module 5. EE project financing and VSUEE project financing approach
15.00 – 15.15 | Breaks
15.15 – 16.15 | Component 6. Case study in EE for Manufacturing Industry: Cement, Steel, Seafood Processing, Brick and Ceramic, Textile, Beverage, Paper & Pulp, Other Industries (Plastics...)
16.15 – 16.45 | Discuss
16.45 – 17.00 | Closing

## Slide 3
Module 6:
Typical report on energy efficiency in cement industry in Vietnam
Dự án Thúc đẩy tiết kiệm năng lượng trong các ngành công nghiệp Việt Nam
TRAINING PROGRAME for IEs
for: Enterprise leaders

## Slide 4
Cement industry

## Slide 5: Content
The facility’s information on the case study
Energy efficiency measures

## Slide 6: 1. General information
Main production field: Cement and clinker production
Main products: Clinker, PCB 30 cement, PCB 40 cement
Production scale: 1 cement production line with a capacity of 4,000 tons of clinker per day
Key energy equipment: Transformer station, air compressor station, circulating pump station...

## Slide 7: Production line
Cement production process
Types of energy used in the production line
Electrical energy is used in systems and equipment such as: crushers, grinders, fans, dust collectors, bagging machines, air conditioning, lighting, and air compressors..
The compressed air distribution system supplies compressed air for controlling pistons in production machines and for processes like dust collection, bagging, and kiln operation.
Coal is used in the clinker firing process in the rotary kiln.
FO oil (fuel oil) is used for kiln startup and as supplemental fuel when necessary.

## Slide 8: Energy supply system
Electrical system
The electrical system of the company uses a 35 kV grid power supply through 13 substations (2 high-voltage substations and 11 low-voltage substations).
Image of measuring equipment at the electrical substation
At the substations, the measurement and monitoring systems are equipped relatively comprehensively. The company has installed both high-voltage and low-voltage power factor correction systems. The power factor correction system ensures that the power factor of the electrical supply system is maintained above 0.9.
Image of substations

## Slide 9: Energy supply system
The company's lighting system is small compared to the scale and energy consumption level.
The company's use of natural light has not been well implemented. Most of the storage facilities do not have transparent roofing to take advantage of natural light. Additionally, the lighting fixtures are positioned quite high, resulting in low illumination intensity.
Lighting system
Some lighting locations of the factory

## Slide 10: Energy supply system
Compressed air system
The company has one independent centralized compressed air station that is connected to the other systems, with valves that are frequently open. It includes 5 screw air compressors, each with a power capacity of 200 kW and operating at a pressure of approximately 7 bar.
Image of the compressed air station

## Slide 11
2
Energy efficiency measures

## Slide 12: Energy efficiency measure number 1
1. Enhancing internal management and equipment maintenance
For the electrical equipment system
Regularly propagate and train employees on energy efficiency. Enhance the involvement of operational staff (Electricity savings should be based on a broad foundation and require the support of operational staff).
Monitor energy consumption based on the number of production and non-production days to identify and address energy loss points. Develop procedures and checklists to ensure that equipment shutdowns have been properly carried out.
Install automatic control devices to turn off equipment when not in use
Turn off all unnecessary lights (such as during breaks, lunch hours, shift changes, and holidays).
Install power factor correction capacitors to create a "leading" power factor to address the "lagging" power factor of equipment. These capacitors can be installed at individual devices or multiple devices to control part or the entire distribution system.
Control the surrounding temperature to extend the insulation lifespan and reliability of the motors. Avoid direct exposure to sunlight, place motors in well-ventilated areas, and keep the motors clean.

## Slide 13: Energy efficiency measure number 1
For the refrigeration and air conditioning systems
Clean and regularly replace filters, clean the evaporator equipment and condenser coils to improve the cooling efficiency of the air conditioning system.
Set the air conditioning system temperature appropriately. The temperature should be set between 26°C and 27°C in summer, and not too high or low. Setting the temperature too low will cause the air conditioner to run longer. Each 1°C reduction in temperature will increase energy consumption by 3-4% of the air conditioning system’s power usage.
For the compressed air system
Train and raise employee awareness to operate and maintain the compressed air system effectively.
Ensure the system remains dry. Ensure proper drainage slope, discharge points, and vents to minimize rusting of pipes.
Invest in leak detection equipment or gas leak testers to measure total leakage and compressor power. Identify and fix any compressed air leaks, and prevent recurrence.

## Slide 14: Energy efficiency measure number 1
  For office buildings
  Check the insulation thickness of walls and roofs.
  Review and seal gaps that lead to heat loss from the rooms.
  Use curtains, both inside and outside windows, to retain heat in winter and keep cool in summer.
  Install sunshades for windows to reduce heat during the summer.
  Install automatic door and gate systems.
  Install double-glazed doors and windbreak doors on the northwest side.
  Set air conditioning to temperatures above 26°C in summer and 23°C in winter.
  Turn off all lighting equipment when not in use or after working hours.

## Slide 15
Install inverters combined with a general controller for the compressor station.
Current situation
The company's compressed air station consists of 5 air compressors, each with a capacity of 200kW (4 running and 1 backup), with manual control and pressure set for each machine from 6.3 to 6.5 bar. The idle running time of the machines is less than 10% of the total running time. When operating in idle mode, the compressors still consume about 40% of their rated power without generating compressed air, leading to energy waste.
Measures
“Install an inverter combined with a centralized controller for the air compressor station” .
Energy efficiency measure number 2

## Slide 16: Energy efficiency measure number 2
Energy consumption of the air compressor station based on the compressed air flow produced.
The chart compares the pressure fluctuations of a compressor with a frequency inverter to those of other compressors.
Install inverters combined with a general controller for the compressor station.

## Slide 17: Energy efficiency measure number 2
Function of the compressor station controller
Automatically operates the compressors in the system based on the compressed air demand of production.
Sets the operating schedule for the compressors to match production times.
Synchronizes operating hours and the number of starts: ensures stable air quality, facilitating maintenance and servicing of the compressor system.
Diagram of the connection of the controller in coordination with the air compressors.
Install inverters combined with a general controller for the compressor station.

## Slide 18
NO | SPECIFICATIONS | UNIT | VALUE
1 | The average electricity price of the company for the first 10 months of 2015 | VND | 1.355
2 | Electricity saved after implementing the measure | kWh/year | 354.816
3 | Income from energy efficiency in one year | Million VND/year | 481
4 | Total investment cost for project implementation | Million VND | 640
5 | Simple payback period | month | 16,0
6 | Discount rate | % | 10
7 | Project lifecycle | year | 10
8 | Net Present Value (NPV) of the project | Million VND | 2937
9 | Internal Rate of Return (IRR) | % | 80%
10 | Payback period of the investment project | tone/year | 40,6
Install inverters combined with a general controller for the compressor station.
Energy efficiency measure number 2

## Slide 19: Energy efficiency measure number 3
Renovating the lighting system
Current situation
The lighting system in the workshop mainly consists of 400W, 250W, and 125W mercury vapor lamps and T8 fluorescent lamps with electromagnetic ballasts. The Company's lighting devices are all low-efficiency equipment, leading to high electricity consumption during use.
Measures
“ Renovating the lighting system”
Implementation plan
Gradually replace 219 400W mercury vapor lamps with 250W sodium vapor lamps.
Gradually replace 176 250W mercury vapor lamps with 150W sodium vapor lamps.
Gradually replace 126 125W mercury vapor lamps with 70W sodium vapor lamps.
Gradually replace 3,170 T8 fluorescent lamps, 1.2m, 36W, with electromagnetic ballasts (12W) with T5 fluorescent lamps, 1.2m, 28W, and electronic ballasts (3.5W), maintaining equivalent brightness.

## Slide 20: Energy efficiency measure number 3
Technical Specifications of Typical Lights
Technical Specifications of Typical Lights
Renovating the lighting system

## Slide 21: Energy efficiency measure number 3
Principles of energy efficiency
Improve lighting efficiency by replacing existing low-efficiency lighting devices with high-efficiency lighting devices while ensuring the necessary lighting quality requirements
250W sodium high-pressure lamps and metal halide fluorescent lamps
Renovating the lighting system

## Slide 22: Energy efficiency measure number 3
No | Specification | Unit | Value
1 | The average electricity price of the company for the first 10 months of 2015 | VND | 1.355
2 | Electricity saved after implementing the measure | kWh/year | 327.439
3 | Income from energy efficiency in one year | Million VND/year | 444
4 | Total investment cost for project implementation | Million VND | 998
5 | Simple payback period | month | 27,0
6 | Discount rate | % | 10
7 | Project lifecycle | year | 4
8 | Net Present Value (NPV) of the project | Million VND | 509
9 | Internal Rate of Return (IRR) | % | 31%
10 | Payback period of the investment project | tone/year | 30,5
Renovating the lighting system

## Slide 23: Energy efficiency measure number 4
Install ENPOSS - DORCE harmonic filter devices for the rectifier system supplying power to the kiln and drying furnace units in lines 1 and 2
Current situation:
Most of the clinker cooling fan devices of the company are equipped with inverters for control, and the fan speed is controlled by the operator depending on the production operating conditions. The inlet and outlet air direction vane valves are fully open (100%) when using the inverter
Measurement results of electricity quality in the drying & firing area
Comment: The harmonic levels in the above areas are all higher than the allowed standard.

## Slide 24: Energy efficiency measure number 4
Measure:
Currently, there are two types of measures for preventing harmonic waves on the market: using inductors (passive components) and using active components (active filters). The active filter emits pulses to reduce the distortion of the power supply.
A widely certified and commonly used product is the ENPOSS product, which can save from 7-15% of electricity consumption (according to the manufacturer's evaluation).
Illustrating the effectiveness of the ENPOSS - FORCE harmonic filter
Install ENPOSS - DORCE harmonic filter devices for the rectifier system supplying power to the kiln and drying furnace units in lines 1 and 2

## Slide 25: Energy efficiency measure number 4
Installation Diagram of FORCE Equipment
Install ENPOSS - DORCE harmonic filter devices for the rectifier system supplying power to the kiln and drying furnace units in lines 1 and 2

## Slide 26: Energy efficiency measure number 4
Calculation results of the measures "Installation of ENPOSS-DORCE harmonic filter equipment for the rectifier power supply system for the kiln and dryer units of line 1,2"
No | Specification | Unit | Value
1 | Average electricity price of the company in the first 9 months of 2015 | VND | 
2 | Energy efficiency after implementing the measures | kWh/year | 
3 | Income from energy efficiency in one year. | Million VND/year | 
4 | Investment cost per harmonic filter device ENPOSS - FORCE. | USD/kW | 
5 | Exchange rate. | VND/USD | 
Install ENPOSS - DORCE harmonic filter devices for the rectifier system supplying power to the kiln and drying furnace units in lines 1 and 2

## Slide 27: Energy efficiency measure number 4
Install ENPOSS - DORCE harmonic filter devices for the rectifier system supplying power to the kiln and drying furnace units in lines 1 and 2
NO | SPACIFICATION | UNIT | VALUE
1 | Average electricity price of the company in the first 9 months of 2015. | VND | 1.355
2 | Electricity saved after implementing the measure | kWh/year | 554.400
3 | Revenue from energy efficiency over one year | Million VND/year | 751,2
4 | Investment cost for ENPOSS - FORCE harmonic filter equipment | USD/kW | 45
5 | Exchange rate | VND/USD | 21.673
6 | Total investment cost for project implementation | Million VND | 1.170
7 | Simple Payback Period | month | 18,7
8 | Discount Rate | % | 10
9 | Project Lifecycle | year | 5
10 | Net Present Value (NPV) of the Project | Million VND | 1947,6
11 | Internal Rate of Return (IRR) | % | 62%
12 | Payback Period | month | 21,0

## Slide 28: Energy efficiency measure number 5
Utilizing the waste heat from the clinker kiln flue gas and the exhaust air from the clinker cooling process to generate electricity
NO | Position | Temperature, oC | Avarage temperatura oC
1 | Cooling Tower | 320-350 | 330
2 | Clinker Cooling | 280-332 | 310

## Slide 29
Principle diagram of the clinker production system
Energy efficiency measure number 5
Utilizing the waste heat from the clinker kiln flue gas and the exhaust air from the clinker cooling process to generate electricity

## Slide 30
Measure: The company invests in a system for utilizing waste heat from the clinker kiln group, using the traditional steam Rankine cycle technology to generate electricity.
Summary of key economic and technical indicators for the power plant system for various clinker kiln capacities
NO | Economic and Technical Specifications of the Power Plant | Unit | Clinker Kiln Index (tons per day) |  | 
 |  |  | 2500T | 4000T | 5000T
1 | Installed Capacity | MW | 4,5 | 7,5 | 9,0
2 | Average Power Generation Capacity | MW | 4,0 | 7,0 | 8,6
3 | Operating time per year ( | Hour | 7200 | 7200 | 7200
4 | Electricity generation per year | MWh | 28800 | 50000 | 62000
5 | Technical Staff for Station Operation | Person | 10 | 10 | 10
6 | Total investment. | Million USD | 9-12 | 15-20 | 18-22
Energy efficiency measure number 5
Utilizing the waste heat from the clinker kiln flue gas and the exhaust air from the clinker cooling process to generate electricity

## Slide 31
The installed capacity of the power generation system is 7.5 MW, with a load factor of 85%. The average generation capacity will be 6.4 MW.
The estimated investment cost is approximately 2.5 million USD per 1 MW of installed capacity.
Energy efficiency measure number 5
Utilizing the waste heat from the clinker kiln flue gas and the exhaust air from the clinker cooling process to generate electricity

## Slide 32
Financial indicators table for investment in energy efficiency measure No. 5.
NO | SPECIFICATION | UNIT | VALUE
1 | Total investment | Million VND | 406.369
2 | Electrical energy saved after implementing the energy efficiency measure | kWh/year | 50.688.000
3 | Average electricity price for the first 10 months of 2015 | VND/kWh | 1.355
4 | Cost savings after implementing the energy efficiency measure. | million VND/year | 68.682
5 | Simple payback period | month | 71
6 | Discount rate | % | 10
7 | Project lifespan | year | 15
8 | Net Present Value (NPV). | Million VND | 256.441
9 | Payback Period | month | 110
10 | Amount of CO2 emissions reduction | Tone /year | 42.035
Energy efficiency measure number 5
Utilizing the waste heat from the clinker kiln flue gas and the exhaust air from the clinker cooling process to generate electricity

## Slide 33: Energy efficiency measure number 6
Installing inverters for the calciner fans 421FN02.
Current situation: The calciner system of the plant is supplied with air by a fan with the model code 421FN02M01, with a design capacity of 132 kW, a rated current (rc) Irc = 231A, rated speed n = 2975 rpm, and voltage 380V. Operating parameters: operating current (oc) Ioc = 138A, actual power consumption is approximately 70 kW.

## Slide 34: Energy efficiency measure number 6
Installing inverters for the calciner fans 421FN02.
According to the fan characteristics, we have:
- Q1 / Q2 = n1 / n2 : The flow rate is directly proportional to the speed.
- H1 / H2 = (n1 / n2)2 : The pressure is proportional to the square of the speed.
- P1 / P2 = (n1 / n2)3 : The power is proportional to the cube of the speed.

## Slide 35: Energy efficiency measure number 6
Proposed measure: Install an inverter for the fan motor (421FN02) with a capacity of 132 kW and input voltage of 380V.
Bảng tính tiềm năng tiết kiệm năng lượng cho giải pháp TKNL số 6
NO | SPECIFICATION | UNIT | VALUE
1 | The average operating hours per day | hour | 24
2 | The average number of operating days per year. 4o mini | day | 330
3 | The total rated power of the equipment. | kW | 132
4 | The total average actual power of the equipment. | kW | 70
5 | The energy consumption of the baseline option. | kWh/year | 554.400
6 | The percentage of energy savings compared to the baseline option. | % | 25,0%
7 | Electrical energy consumption after implementing the measure. | kWh/year | 415.800
8 | Energy efficiency after implementing the measure. | kWh/year | 138.600
9 | Reduction in CO2 emissions | tone/year | 75,0
Installing inverters for the calciner fans 421FN02.

## Slide 36: Energy efficiency measure number 7
Install an inverter for the exhaust fan of the grinding system 541FN03
Current situation: The cement grinding machine has a fan with model number 541FN03M01, with a design power of 850 kW and an input voltage of 6 kV. Working parameters: working current Ilv = 64, actual power consumption is approximately 645 kW. The damper opening depends on the load, the kiln output, and is controlled by the operator from the central control room, with the intake damper opened at 60%. The actual working airflow of the fan is about 70% of the rated airflow. This load level is maintained regularly, accounting for up to 90% of the fan's operating time.

## Slide 37: Energy efficiency measure number 7
Measure: Install a variable frequency drive (VFD) for a fan motor (541FN03) with a power rating of 850 kW and an input voltage of 6 kV.
Install an inverter for the exhaust fan of the grinding system 541FN03

## Slide 38: Energy efficiency measure number 7
Table of financial indicators for the investment in energy efficiency measure No. 7
NO | SPECIFICATION | UNIT | VALUE
1 | The average electricity price of the company in the first 9 months of 2015. | VND | 1.355
2 | The electrical energy saved after implementing the energy efficiency measure. | kWh/year | 1.021.680
3 | The income generated from energy efficiency in one year. | Million VND/year | 1.384
4 | The total investment cost to implement the project. | Million VND | 3.150
5 | The simple payback period. | month | 27,3
6 | Discount rate. | % | 10
7 | Project lifetime. | year | 10
8 | Net Present Value (NPV) of the project. | Million VND | 7150
9 | Internal Rate of Return (IRR) of the project. | % | 47%
10 | The payback period of the project. | month | 38,7
Install an inverter for the exhaust fan of the grinding system 541FN03

## Slide 39
Dự án Thúc đẩy tiết kiệm năng lượng trong các ngành công nghiệp Việt Nam
THANK YOU