## Slide 1: TRAINING PROGRAME for IEs
The Vietnam Scaling up Energy Efficiency Project (VSUEE)
for: Enterprise leaders

## Slide 2: Training program for business leaders
TIME | Content
8.00 – 8.30 | Registration
8.30 – 8.40 | Opening Remarks
8.40 – 9.45 | Module 1: Project introduction Policy introduction: energy saving, greenhouse gas emission reduction, gender issues related in EE
9.45 – 10.00 | Breaks
10.00– 11.00 | Module 2. Relations between energy, environment and production and business, use of clean energy
11.00 – 11.45 | Module 3. The current situation of energy use and potential of industrial waste in Vietnam (cement, steel, seafood processing, brick and ceramic, textiles, beverages, paper and pulp, other industries (plastics...)
11.45 – 12.00 | Discuss
12.00 – 13.30 | Lunch
13.30 – 14.15 | Module 4. Energy Management, Energy Management System
14.15 – 15.00 | Module 5. EE project financing and VSUEE project financing approach
15.00 – 15.15 | Breaks
15.15 – 16.15 | Component 6. Case study in EE for Manufacturing Industry: Cement, Steel, Seafood Processing, Brick and Ceramic, Textile, Beverage, Paper & Pulp, Other Industries (Plastics...)
16.15 – 16.45 | Discuss
16.45 – 17.00 | Closing

## Slide 3
Module 6:
Typical report on energy efficiency in paper and pulp industry in Vietnam
Dự án Thúc đẩy tiết kiệm năng lượng trong các ngành công nghiệp Việt Nam
TRAINING PROGRAME for IEs
for: Enterprise leaders

## Slide 4: Content
The facility’s information on the case study
Energy efficiency measures

## Slide 5
1
The facility’s information on the case study

## Slide 6: General information
Main production sector: Paper manufacturing
Main products: Printing paper, photocopy paper, writing paper
Main energy equipment: transformer station, compressed air station, circulating pump station, production machinery…

## Slide 7: Production line
Production process
Hydraulic grinding
Storage tank
Disc milling
Storage tank
Machine tank
Boiler
Winding
Finished product
Stuff box
Paper machine
Stuff box
steam
Chemical
coal
water
Chemical
Sell
Impregnated powder
Water
Drainage

## Slide 8: Production line
  Types of energy used in the production line:
Electricity is used in systems and equipment such as: crushers, conveyors, pump motors, mixers; fans,...
The compressed air distribution system supplies compressed air for controlling pistons in production machines
Coal is used for boilers.

## Slide 9: Energy supply system
The company's electrical system uses a 35 kV power grid through 3 transformers
Picture of measuring equipment at the power station
At the substations, the monitoring measurement system is relatively well-equipped. The company has installed high-voltage and low-voltage power factor correction systems, ensuring that the power factor of the power supply system always exceeds 0.9.
Picture of the transformer station
1. Electrical system

## Slide 10: Energy supply system
The company's lighting system is large in scale, consisting of fluorescent lamps and high-pressure halogen lamps. High-pressure lamps are used for the workshop area and street lighting, while fluorescent lamps are used for office lighting.
The workshop roof system is equipped with natural daylighting panels, helping to save electricity for the general lighting system during the day
Some lighting locations of the factory
2. Lighting system

## Slide 11: Energy supply system
The company has a 55 kW screw air compressor to serve its production activities.
The air compressor operates continuously in load/unload mode with an operating pressure of 5.5 ÷ 6.5 bar. When the pressure reaches 6.5 bar, the compressor switches to unload mode, and when the compressed air pressure drops below 5.5 bar, the compressor loads and switches to load mode.
Compressed air station diagram.
3. Air compressor system

## Slide 12
2
Energy efficiency measures (EEMs)

## Slide 13: EEMs1: Enhance internal management and equipment maintenance.
1. For the electrical equipment system.
Regularly propagandize and train employees on EE. Strengthen the involvement of operational staff (Electricity savings should be based on a broad foundation and supported by operational staff).
Monitor energy consumption based on production and non-production days to identify and address energy loss points. Develop procedures and inspection checklists to ensure that equipment shutdowns have been carried out.
Install automatic control devices to turn off equipment when not in use.
Turn off all unnecessary lights (such as during break times, lunch hours, shift changes, and holidays).
Install capacitors to create a "leading" power factor to correct the "lagging" power factor of equipment. These capacitors can be installed on individual devices or on several devices to control part or the entire distribution system.
Control the ambient temperature to extend the insulation life and reliability of the motor. Avoid placing the motor under direct sunlight, install the motor in well-ventilated areas, and keep the motor in a clean condition.

## Slide 14: EEMs1: Enhance internal management and equipment maintenance.
2. For the refrigeration and air conditioning system.
Regularly clean and replace filters, clean the evaporator and the condenser coil to improve the cooling efficiency of the air conditioning system.
Set the air conditioning system temperature to a reasonable level. The air conditioning temperature should be set at 26°C ÷ 27°C in the summer, and should not be set lower or higher. Setting the temperature too low will cause the air conditioner to run longer. For every 1°C reduction in temperature, energy consumption increases by 3 - 4% of the air conditioning system's energy use.
3. For the air compressor system.
Train and raise employeee awarness to operate and maintain the air compressor system effectively.
Ensure the system is dry. Make sure that the drain slope, discharge points, and venting points are properly maintained to minimize the risk of pipe corrosion.
Invest to buy leak detection equipment / leak detection machines to measure total losses through the compressed air system and compressor power. Identify and address air leakage points and prevent recurrence.

## Slide 15: EEMs1: Enhance internal management and equipment maintenance.
4. For the office building
Check the insulation thickness of walls and roofs.
Inspect and seal any gaps that cause heat loss from the room.
Use curtains inside and outside of windows to retain heat in winter and provide cooling in summer.
Install sunshades for windows to reduce summer heat.
Install automatic door and gate closers.
Install double-glazed doors and windbreak doors on the west-north sides.
Set the air conditioning temperature above 26°C in summer and 23°C in winter.
Turn off all lighting when not in use or after work hours.

## Slide 16: EEMs 2: Monitor, inspect, and address air leakage points in the system.
Current status.
Through the survey and inspection of compressed air leaks at the company, the auditing unit detected leaks at control valves, fittings, and pneumatic cylinder valve actuators.
Locations with many compressed air leakage points :
+ At the pneumatic valves of the machinery and equipment
+ At the fittings on the compressed air pipeline from the air compressor station to the usage points.
Detailed statistics of the company's leakage points across 22 large and small air leakage points
Measure
“Monitor, inspect, and address compressed air leakage points.”

## Slide 17: EEMs 2: Monitor, inspect, and address air leakage points in the system.
Compressed air leakage detection device and example
NO | Specification | Unit | Value
1 | Average electricity price | VND | 1.575
2 | Electricity saved after implementing the measure | kWh/year | 25.230
3 | Income from energy efficiency in one year. | Million VND/year | 40
4 | Total investment cost for project implementation | Million VND | 40
5 | Simple payback period | month | 12
6 | Discount factor | % | 10
7 | Project lifecycle | year | 4
8 | Reduce CO2 emissions | tonne/year | 23

## Slide 18: EEMs 3: Improve the operational efficiency of air compressors
Current status
The company uses a 55kW air compressor to supply air for the production line. The operating condition of the air compressors is as follows:
Operating time: The air compressor operates continuously 24 hours a day.
The compressed air pressure set at the station is 5.5 bar – 6.5 bar.
Measure: “ Improving the operational efficiency of air compressors”
Implementation plan: The inverter will control the frequency of the electric current to always meet the minimum pressure requirements. When there is a change in usage demand, the compressed air pressure will fluctuate. At this point, the inverter will control the speed to promptly meet the demand. The inverter makes the machine's operation more responsive, immediately adjusting to even small changes in pressure.

## Slide 19: EEMs 3: Improve the operational efficiency of air compressors
Chart comparing the operating condition of the air compressor before and after installing the inverter
Energy efficiency calculation
NO | Specification | Unit | Value
1 | Average electricity price | VND | 1.575
2 | Electricity saved after implementing the measure. | kWh/year | 31.752
3 | Income from energy efficiency in one year. | Million VND/year | 50
4 | Total investment cost for project implementation | Million VND | 170
5 | Simple payback period | month | 41
6 | Discount factor | % | 10
7 | Reduce CO2 emissions | tons/year | 29

## Slide 20: EEMs 4: Install the CESS electricity-saving device for transformer No. 1
Current situation:
The transformer supplies power to the equipment system in the production line, with the main load being the production technology equipment. The system's primary load consists of motors.
Transformer power measurement results
NO | Transformer | Actual load (kW) | Voltage harmonic(%) | Current harmonic(%)
1 | 1.800 kVA machine | 709 | 5 | 29
2 | 250 kVA machine | 61 | 5 | 8
3 | 1.000 kVA machine | 630 | 2 | 8

## Slide 21: EEMs 4: Install the CESS electricity-saving device for transformer No. 1
Measure:
The CESS product has the following electricity-saving mechanism
Improve the conversion efficiency of the machinery and equipment system that transforms electrical energy into light energy, heat energy, or mechanical energy.
Enhance the efficiency of electrical transmission from the power supply station to the electrical devices and machinery.
Improve the power factor of the system, helping to increase the useful power of the equipment system.
CESS device and installation method

## Slide 22: EEMs 4: Install the CESS electricity-saving device for transformer No. 1
Calculation results for the measure 'Install CESS EE device for transformer number 1'
NO | SPECIFICATION | UNIT | VALUE
1 | Average electricity price | VND | 1.575
2 | The electricity saved after implementing the measure. | kWh/year | 265.450
3 | The income generated from energy efficiency in one year | Million VND/year | 418
4 | Exchange rate | VND/USD | 24.283
5 | Total investment cost for implementing the project. | Million VND | 1.278
6 | Simple payback period | month | 36,7
7 | CO2 emission reduction | tons/year | 242

## Slide 23: EEMs 5: Insulate the steam piping
Current situation:
Steam is primarily used for the production process. Currently, the main steam pipe at the boiler, with a length of 3.5 meters, has old and damaged insulation layers that have not been replaced, leading to significant heat loss.
The location of the damaged insulation

## Slide 24: EEMs 5: Insulate the steam piping
Measure:
With the current situation above, the proposed EE measure is: "Insulating the steam pipe."
This is a low-investment energy measure with high economic efficiency and ease of implementation. There are many types of insulation materials available on the market for insulating pipe surfaces, such as fiberglass, rockwool, etc. Below are some commonly used insulation materials in practice
Some typical insulation materials
Glass wool
Rock wool
Ceramic wool

## Slide 25: EEMs 5: Insulate the steam piping
Table for calculating the financial indicators for the investment in EE measure number 5.
NO | SPECIFICATION | UNIT | VALUE
1 | Total investment | million VND | 50
2 | The heat energy saved after implementing the energy efficiency measure | kWh/year | 175.457
3 | Average electricity price | VND/kWh | 2.203
4 | The cost saved after implementing the energy efficiency measure | million VND/year | 49
5 | Simple payback period | month | 12
7 | Project lifespan | year | 5
8 | Net Present Value (NPV) | million VNĐ | 154
9 | Amount of CO2 emission reduction | tons /year | 62
The calculation results for energy efficiency measure number 5

## Slide 26: EEMs 6: Install an air dryer utilizing exhaust gas heat for the boiler
Current status:
The company uses one boiler with a capacity of 10 T/h, and the overall system steam pressure is approximately 7 bar. The boiler uses 4b anthracite coal as fuel.
Currently, the company's air-drying system is broken and not operational
The exhaust gas temperature after the economizer is above 200°C and is not being utilized
The results of the analysis of the flue gas from the boiler after the economizer
The picture of the combustion air supply being bypassed through the air heater

## Slide 27: EEMs 6: Install an air dryer utilizing exhaust gas heat for the boiler
Current status:
Energy calculation results based on boiler exhaust gas before implementing the measure
Look up flue gas and fuel specifications
Enter input parameters
Select fuel type
Enter the fly ash coefficient
Amount of fuel used
Enter flue gas temperature.
Enter the excess air coefficient
Result
Actual air enthalpy
Actual flue gas enthalpy
Flue gas energy
Theoretical dry flue gas volume
Theoretical wet flue gas volume
Actual flue gas volume

## Slide 28: EEMs 6: Install an air dryer utilizing exhaust gas heat for the boiler
Measure:
Install an air dryer utilizing exhaust gas heat for the boiler
Energy efficiency potential
The exhaust gas temperature of the boiler after the economizer at 200°C can be reduced to 155°C to save energy
Structure of the air dryer.
Energy calculation results based on boiler exhaust gas after implementing the measure
Bach Khoa Energy Efficiency Joint Stock Company
KTV: Than Van Toan
Look up flue gas parameters of fuel
Enter input parameters
Select fuel type
Enter the fly ash coefficient
Amount of fuel used
Enter flue gas temperature
Enter the excess air coefficient
Result
Coal
Actual air enthalpy
Actual flue gas enthalpy
Flue gas energy
Theoretical dry flue gas volume
Theoretical wet flue gas volume
Actual flue gas volume
Incoming smoke
Exhaust air
Incoming air
Exhaust smoke
Air

## Slide 29: EEMs 6: Install an air dryer utilizing exhaust gas heat for the boiler
EE potential calculation table for EEMs number 6
NO | SPECIFICATION | UNIT | VALUE
1 | Average operating hours per day | hour | 24
2 | Average operating days per year | day | 300
3 | Average annual coal consumption of the boiler | Tons/year | 5.937
4 | Exhaust gas temperature before implementing the measure | oC | 200,00
5 | Exhaust gas temperature after implementing the measure | oC | 155
6 | Investment cost | Million VND | 530
7 | Energy efficiency ratio after implementing the measure | % | 2,50
8 | Amount of coal saved after implementing the measure | Tons/year | 148
9 | Energy efficiency income in one year | Million VND | 326,99
10 | Payback period | Month | 19,45
11 | Reduce CO2 emissions | Tons/year | 413,57

## Slide 30
Dự án Thúc đẩy tiết kiệm năng lượng trong các ngành công nghiệp Việt Nam
Thank you