## Slide 1: TRAINING PROGRAME for IEs
The Vietnam Scaling up Energy Efficiency Project (VSUEE)
for: Enterprise leaders

## Slide 2: Training program for business leaders
TIME | Content
8.00 – 8.30 | Registration
8.30 – 8.40 | Opening Remarks
8.40 – 9.45 | Module 1: Project introduction Policy introduction: energy saving, greenhouse gas emission reduction, gender issues related in EE
9.45 – 10.00 | Breaks
10.00– 11.00 | Module 2. Relations between energy, environment and production and business, use of clean energy
11.00 – 11.45 | Module 3. The current situation of energy use and potential of industrial waste in Vietnam (cement, steel, seafood processing, brick and ceramic, textiles, beverages, paper and pulp, other industries (plastics...)
11.45 – 12.00 | Discuss
12.00 – 13.30 | Lunch
13.30 – 14.15 | Module 4. Energy Management, Energy Management System
14.15 – 15.00 | Module 5. EE project financing and VSUEE project financing approach
15.00 – 15.15 | Breaks
15.15 – 16.15 | Component 6. Case study in EE for Manufacturing Industry: Cement, Steel, Seafood Processing, Brick and Ceramic, Textile, Beverage, Paper & Pulp, Other Industries (Plastics...)
16.15 – 16.45 | Discuss
16.45 – 17.00 | Closing

## Slide 3
Module 6:
Typical report on energy efficiency in industries in Vietnam
Dự án Thúc đẩy tiết kiệm năng lượng trong các ngành công nghiệp Việt Nam
TRAINING PROGRAME for IEs
for: Enterprise leaders

## Slide 4
Textile and garment industry

## Slide 5: Content
The facility’s information on the case study Energy efficiency measures (EEMs)

## Slide 6
1
The facility’s information on the case study

## Slide 7: General Information
Main Products: Finished stretch fabric.
Production Scale: Two factories divided into multiple areas for storing raw materials, finished products, etc.
Key Energy Equipment: Weaving machines, dyeing machines, transformer stations, air compressor stations, cooling towers, refrigeration systems, etc.

## Slide 8: Production Line
Production Process

## Slide 9: Production Line
Types of Energy Used in the Production Line:
• Electricity: Used in systems and equipment such as rolling machines, looms, dyeing machines, ventilation systems, packaging, air conditioning, lighting, air compressors, etc.
• Compressed Air Distribution System: Supplies compressed air for controlling pistons in production machines and packaging processes.
• Heat Energy: Used to power dyeing machines, stenter machines, washing machines, etc.
• Diesel Oil (DO): Used for backup generators.

## Slide 10: Power Supply System
The power system uses a 22 kV grid power source through 4 substations.
Cosφ watch image
At the substations, the measurement and monitoring system is relatively fully equipped. Equipped high-voltage and low-voltage cos compensation system, the cosφ compensation system always ensures that the power factor of the power supply system reaches above 0.9.
Pictures of distribution cabinets
Electrical System

## Slide 11: Power Supply System
The company has 4 pneumatic stations divided into 2 factories, independently concentrated and connected together and with valves that are regularly opened.
Including 1 screw compressor with a capacity of 22 kW, 2 GA75VSD compressors with a capacity of 80 kW, and 1 GA22VSD compressor with a capacity of 22 kW with a working pressure of about 8 bar.
Pic of Air Compressor
Air Compressor System

## Slide 12: Power Supply System
The lighting system is quite large, corresponding to the use of most of the electricity consumed. The implementation of turning off/on lighting equipment in non-working areas is well managed and implemented. Regular cleaning of lighting equipment should be strengthened to ensure light for the production area
Hệ thống chiếu sáng

## Slide 13: Power Supply System
The cooling tower system is responsible for cooling the condensate water of the refrigeration system. Each cooling tower will cool a chiller with a cooling capacity of 664 kWh or 400 kWh.
Circulating cooling water system
Cooling tower system and refrigeration system

## Slide 14
2
Energy efficiency measures (EEMs)

## Slide 15: EEMs 1: Enhancing Internal Management and Equipment Maintenance
1. For Electrical Systems:
Regularly promote and train employees on energy-saving practices. Increase the involvement of operational staff (Energy-saving efforts should be broad-based and supported by operational personnel).
Monitor energy consumption based on production and non-production days to identify and address energy loss points. Develop procedures and checklists to ensure equipment shutdowns are properly executed.
Install automatic control devices to switch off equipment when not in use.
Turn off all unnecessary lighting (e.g., during breaks, lunch hours, shift changes, or non-working days).
Install power factor correction capacitors to address lagging power factors in equipment. These can be installed on individual devices or groups of equipment to control part or all of the distribution system.
Control ambient temperature to extend the lifespan of insulation and improve motor reliability. Avoid exposing motors to direct sunlight, place them in well-ventilated areas, and keep them clean.

## Slide 16: EEMs 1: Enhancing Internal Management and Equipment Maintenance
2. For Cooling and Air Conditioning Systems
Regularly clean and replace filters, and clean evaporators and condenser coils to improve the cooling efficiency of air conditioners.
Set a reasonable temperature for air conditioning systems. During summer, the temperature should be set between 26°C and 27°C. Avoid setting it too low or too high, as excessively low temperatures cause the air conditioning to operate longer. Each 1°C reduction in temperature increases energy consumption by 3–4%.
3. For Compressed Air Systems
Train and raise employee awareness for efficient operation and maintenance of the compressed air system.
Ensure the system remains dry. Maintain proper drainage slopes, drain points, and outlets to prevent pipe corrosion.
Invest in leak detection equipment/devices to measure total energy loss in the compressed air system and compressor capacity. Identify and repair leaks in the compressed air system to prevent recurrence.

## Slide 17: EEMs 1: Enhancing Internal Management and Equipment Maintenance
4. For Office Buildings
Inspect the thickness of wall and roof insulation layers.
Check and seal any gaps that cause heat loss from rooms.
Use interior and exterior curtains to retain heat in winter and cool air in summer.
Install window sunshades to reduce heat during summer.
Install automatic door and gate closers.
Install double-layer doors and air curtains on west-facing and northwest-facing directions.
Set air conditioners to temperatures above 26°C in summer and 23°C in winter.
Turn off all lighting when not in use or after working hours.

## Slide 18: EEMs 2: Monitoring and Repairing Compressed Air Leaks
Current Status
Through surveys and inspections of compressed air leaks at the company, the audit team identified leaks in control valves, connectors, and pneumatic cylinder valve mechanisms. Compressed air leaks are inevitable during the operation of air compressors. Common locations where compressed air leaks are frequently detected include:
Pneumatic valves in machinery systems.
Connectors.
Solution
Implement the approach: “Monitoring and Repairing Compressed Air Leaks” to address the identified issues.

## Slide 19: EEMs 2: Monitoring and Repairing Compressed Air Leaks
Technical Specifications:
• Brand: Allsun
• Model: EM282
• Color: White & Black
• Frequency Response: 40kHz ± 2kHz
• Battery Type: 9V battery (not included)
• Operating Temperature: 0–40°C
• Product Weight: 80g
• Product Dimensions: 191 x 50 x 29mm
Pneumatic Leak Detector

## Slide 20: EEMs 2: Monitoring and Repairing Compressed Air Leaks
TT | PARAMETER | UNIT | VALUE
1 | Average electricity price | VNĐ | 1.691
2 | Pressure | bar | 6,9
3 | Amount of leakage according to the size of the leak | m³/minute | 0,0453
4 | Number of Leak Points | point | 20
5 | Average electricity consumption to produce a m3 of compressed air | kWh/m3 | 0,12
6 | Total Leaks/Year | m³/năm | 326.160
7 | Electricity saved after implementing the solution | kWh/năm | 39.139
8 | Income brought by energy saving in 1 year | Triệu VNĐ/năm | 66,2
9 | Total investment cost for project implementation | Triệu VNĐ | 34
10 | Simple payback period | tháng | 6,2

## Slide 21: EEMs: Installing an IFC System to Control Airflow and EE in the Compressed Air System
Current Situation:
The factory’s compressed air system consists of two screw compressors, which are used to control the opening and closing valves in the production line and for certain production stages.
During the survey, it was observed that the company operates two compressors: one in Workshop 1 and another in Workshop 2.
Solution: Install an IFC system to control airflow and optimize energy consumption in the compressed air system.
IFC Equipment System

## Slide 22: EEMs: Installing an IFC System to Control Airflow and EE in the Compressed Air System
Actual installation image of IFC equipment system
Installation diagram of the IFC equipment system at the outlet of the air compressor station
Compressed Air System
Gas Treatment Equipment

## Slide 23: EEMs: Installing an IFC System to Control Airflow and EE in the Compressed Air System
No | Parameter | Unit | Value
1 | Average electricity price | VNĐ/kWh | 1.691
2 | Power consumption before implementing the solution | kWh/year | 1.101.600
3 | Investment Rate | USD/kW | 90
4 | Total cost of investment in equipment to implement the solution | million VNĐ | 448
5 | Percentage of system savings when implementing the solution | % | 7,5
6 | Electricity consumption after implementing the solution | kWh/year | 1.018.980
7 | Electricity saved after implementing the solution | kWh/year | 82.620
8 | Income brought by saving energy in 1 year | million VNĐ/year | 139,7
9 | Simple payback period | month | 38,5
10 | Project lifespan | year | 10

## Slide 24
Dự án Thúc đẩy tiết kiệm năng lượng trong các ngành công nghiệp Việt Nam
THANK YOU