## Slide 1: TRAINING PROGRAME for IEs
The Vietnam Scaling up Energy Efficiency Project (VSUEE)
for: Enterprise leaders

## Slide 2: Training program for business leaders
TIME | Content
8.00 – 8.30 | Registration
8.30 – 8.40 | Opening Remarks
8.40 – 9.45 | Module 1: Project introduction Policy introduction: energy saving, greenhouse gas emission reduction, gender issues related in EE
9.45 – 10.00 | Breaks
10.00– 11.00 | Module 2. Relations between energy, environment and production and business, use of clean energy
11.00 – 11.45 | Module 3. The current situation of energy use and potential of industrial waste in Vietnam (cement, steel, seafood processing, brick and ceramic, textiles, beverages, paper and pulp, other industries (plastics...)
11.45 – 12.00 | Discuss
12.00 – 13.30 | Lunch
13.30 – 14.15 | Module 4. Energy Management, Energy Management System
14.15 – 15.00 | Module 5. EE project financing and VSUEE project financing approach
15.00 – 15.15 | Breaks
15.15 – 16.15 | Component 6. Case study in EE for Manufacturing Industry: Cement, Steel, Seafood Processing, Brick and Ceramic, Textile, Beverage, Paper & Pulp, Other Industries (Plastics...)
16.15 – 16.45 | Discuss
16.45 – 17.00 | Closing

## Slide 3
Module 6:
Typical report on energy efficiency in seafood industry in Vietnam
Dự án Thúc đẩy tiết kiệm năng lượng trong các ngành công nghiệp Việt Nam
TRAINING PROGRAME for IEs
for: Enterprise leaders

## Slide 4
Seafood industry

## Slide 5: Content
The facility’s information on the case study Energy efficiency measures

## Slide 6
1
The facility’s information on the case study

## Slide 7: General Information
Main Production Field: Seafood Production
Main Products: Various types of sushi shrimp, nobashi shrimp, frozen shrimp, steamed shrimp, breaded shrimp, shrimp paste, etc., packaged for export.
Production Scale: Output exceeding 8,500 tons (in 2022).
Main Energy Equipment: Transformer station, compressed air system, refrigeration system, conveyor belts, steam cookers, boilers, etc.

## Slide 8: Production Line
Production Process
1
Receiving raw materials
Wash 1
Picking the head
Wash 2
Classify
Sizing
Wastewater
Solid waste (casing, head)
Wastewater
Wash 3
Allocate
Mold Placement
Additive processing or as required
Freezing
Preparation
Wastewater
Đóng gói
Solid Waste
Frozen storage, Export
Warehousing
1

## Slide 9: Production Line
Types of Energy Used in the Production Line:
Electricity is used in most of the equipment in the factory, such as the production line; refrigeration compressors, air compressors, pump systems, fans, lighting, etc.
Compressed air is primarily supplied for grading machines and other processes utilizing compressed air within the factory.

## Slide 10: Power Supply System
The power system is supplied by 04 transformers with a capacity of 1,650 KVA - 22/0.4kV
Pictures of backup generators
In order to ensure the stability of the power grid and ensure that the power factor requirements are met, the company has arranged a power factor compensation cabinet. The company's cosφ coefficient is always above 0.9. In addition, the Company uses a generator with a capacity of 1200kVA, in case of a power outage
Substation pictures
1. Electrical System

## Slide 11: Power Supply System
2. Lighting System
The company’s lighting system uses 1,170 50W round LED bulbs. The average usage time of the bulbs is approximately 10 to 12 hours.
The lighting system is equipped with high luminous efficacy LED bulbs, which are energy-efficient. However, compared to the standard lighting levels, most areas suffer from insufficient lighting. The company needs to enhance the cleaning of the lighting system and install reflectors to improve lighting performance.
Lighting at the company

## Slide 12: Power Supply System
3. Boiler System
The company uses four oil-fired boilers, including one 500kg boiler, one 600kg boiler, and two 1-ton boilers.
The boilers do not have an oil preheating system or condensate recovery system. Currently, two boilers are in operation, and the other two serve as backup for the shrimp steaming area.
The output temperature at the boiler area is 200°C, while the temperature used in the shrimp steaming area is 120°C.
Boiler system at the enterprise

## Slide 13: Power Supply System
4. Air Compressor System
The company is using three air compressors with motor capacities of 11kW and 15kW, running in rotation. The set pressure is 8 bar. The compressors are not equipped with ducts to vent hot air from the compressors to the outside environment.
Images of air compressors and accumulators

## Slide 14: Power Supply System
5. Refrigeration System
Factory 1 uses 9 refrigeration compressors, including:
High-capacity compressors (No. 1 and 2)
Compressors No. 3 and 4 supply cooling for the storage and flake ice production
Compressors No. 5 and 6 supply cooling for the contact freezer
Compressors No. 7, 8, and 9 supply cooling for the freezing conveyor belt
Among these, compressors No. 1, 2, 3, and 4 use soft starters, while the others use direct starting.
Refrigeration Compressor Images

## Slide 15
2
Energy efficiency measures

## Slide 16: EEMs 1: Strengthen internal management and equipment maintenance
1. For the refrigeration system:
Strengthen control of non-condensable gases and oil in the refrigerant. This will help increase the efficiency of the refrigeration compressors and improve the cooling effectiveness of the condenser coils.
Install variable frequency drives (VFD) for the cooling fan system of the condenser.
Install a cold storage tank for 10°C chilled water and a cold water supply for the factory air conditioning system.
Install variable frequency drives (VFD) for the refrigeration compressor system.
Increase the frequency of cleaning the exterior of the condenser piping, at least once every 3 months.
Isolate the steam boiler area from the surrounding environment to prevent heat from the boiler from increasing energy consumption in the refrigeration compressor system.

## Slide 17: EEMs 1: Strengthen internal management and equipment maintenance
2. The air compressor system:
Change the location of the compressor station: This is due to the impact of the oil station, which can reduce the operating efficiency of the air compressors and increase the dust accumulation on the compressor filters. Additionally, it poses a safety risk as the area is close to a potential fire hazard.
Reorganize the layout of equipment: Air Compressor → Air Dryer → Air Compressor Receiver Tank → Receiver Tank → Air Dryer to reduce energy consumption of the air dryer.
Install a hot air exhaust hood on top of the compressor to vent heat outside; check and fix any compressed air leaks.

## Slide 18: EEMs 1: Strengthen internal management and equipment maintenance
3. For the office building:
Check the thickness of the wall and roof insulation layers.
Inspect and seal any gaps that cause heat loss from the room.
Use both internal and external curtains to retain heat during winter and cool the room in summer.
Install sunshades for windows to reduce summer heat.
Install automatic door and gate closing devices.
Install double-layer doors and windbreak doors for the west and northwest directions.
Set the air conditioner temperature to above 26°C in summer and 23°C in winter.
Turn off all lighting equipment when not in use or after working hours.

## Slide 19: EEMs 2: Optimizing the Air Compressor System
Current Status:
The company uses 3 air compressors with capacities of 11kW and 15kW. The compressors operate alternately at full capacity. There are no pipes to direct hot air outside. Additionally, the compressor system is located in a rather enclosed room alongside the oil tank. This setup can reduce the compressor’s performance, increase dust buildup on the filters, and compromise system safety due to proximity to fire hazards.
Currently, the air compressor system is arranged as follows: Air Compressor → Air Dryer → Air Receiver.
Solution:
Re-arrange the system order to: Air Compressor → Air Receiver → Air Dryer.
Relocate the compressor station to a different area.

## Slide 20: EEMs 2: Optimizing the Air Compressor System
Current Status:
The company is currently using air fittings, air splitters, and an air piping system for the production area. These fittings all have quick connectors at the outlets, which are prone to air leaks. This is the most common issue with the connectors. The air leakage is caused by: pressure distorting the connectors, improper installation with incorrect pressure tolerance, and the use or misuse of sealing materials (sealant, gaskets, foam rubber, adhesives, etc.).
The connectors used in water or air environments are easily corroded, leading to leaks and breakage. The leakage losses have resulted in a reduction in the end pressure of the air distribution pipeline, necessitating the addition of more compressors to meet production needs. Additionally, air leaks are also increased due to the spray nozzles placed in certain areas for cleaning workers, which also contribute to air leakage.
The air compressor system has not been installed with hot air exhaust pipes, and the high temperatures emitted by the compressors into the environment affect their operating efficiency.
Solution:
Regularly check and detect air leaks, and gradually replace valves, fittings, air splitters, leaking pipes, etc.
Install additional hot air exhaust pipes to direct the heated air from the compressors outside the machine room.

## Slide 21: EEMs 3: Inverter Installation for Refrigeration Compressor
Current Status:
Factory 1 uses 9 refrigeration compressors, which include: high-pressure compressors (1 and 2); compressors 3 and 4 for the warehouse and flake ice; compressors 5 and 6 for contact freezing; and compressors 7, 8, 9 for the freezing conveyor system. Compressors 1, 2, 3, and 4 use soft starters, while the others use direct starting.
Factory 2 also uses 9 refrigeration compressors, which include: low-pressure compressors (1 and 2); high-pressure compressors (5 and 6); compressor 5 for factory 2, serving various processes such as batter coating, cutting, shrimp frying, finished sushi, and storage; compressors 3, 4, and 7 for the cold storage and flake ice; and compressors 8 and 9 for the freezing conveyor system. Compressors 5, 6, 7, and 8 use soft starters, while the others use direct starting.
The compressors without soft starters are operated in direct on-off mode, which causes voltage drops, reduces power quality, and affects other equipment.
The starting current of the refrigeration compressors is significantly higher, more than twice the normal operating current, which impacts the operation of surrounding equipment and affects the overall electrical quality of the company.

## Slide 22: EEMs 3: Inverter Installation for Refrigeration Compressor
Inverter installation diagram into a sample refrigeration compressor system
Solution: Install variable frequency drives (VFDs) for the refrigeration compressor system.
Benefits of the Solution:
The VFD allows the compressors to operate within optimal speed ranges, ensuring flexible adjustment and optimal operation based on load demand.
Operates based on temperature control: The VFD integrates a PID controller that calculates the temperature of the refrigerant based on pressure measurements and adjusts the compressor’s operation accordingly.
Reduces the number of start-stop cycles, extending the lifespan of the compressors.
Soft starts, controlling speed across a continuous range, which avoids the impact of high starting currents.
Provides motor protection functions in case of issues such as overcurrent, overvoltage, phase loss, etc.

## Slide 23: EEMs 3: Inverter Installation for Refrigeration Compressor
- Results of calculating the energy benefits of the solution:
No. | Item Description | Unit | Value
1 | Baseline Data |  | 
1.1 | Actual power of cooling compressors (Unit 1 without soft starters - compressors 5, 6, 7, 8, 9) | kW | 370.2
1.2 | Actual power of cooling compressors (Unit 2 without soft starters - compressors 1, 2, 3, 4, 9) | kW | 398.6
1.3 | Average operating hours per day | Hours | 24
1.4 | Average operating days per year | Days | 352
1.5 | Utilization factor | K | 0.9
1.6 | Simultaneous utilization factor | K | 0.8
1.7 | Annual energy consumption | kWh | 4 676 515
No. | Item Description | Unit | Value
2 | Energy Savings Potential |  | 
2.1 | Energy savings rate after installing variable frequency drives (VFD) for the cooling system | % | 12
2.2 | Energy savings | kWh | 561182
2.3 | Average electricity price | VND (1000) | 1692
2.4 | Cost savings | VND (1000) | 949520
2.5 | Investment cost | VND (1000) | 1 600 000
2.6 | Simple payback period | Years | 1.7
3 | Environmental Impact |  | 
3.1 | Conversion to TOE (Tons of Oil Equivalent) | TOE | 86.6
3.2 | CO₂ emissions reduction | Tons of CO₂ | 405.2

## Slide 24: EEMs 4: Installation of inverter for condenser cooling fan system
Current Status:
The company uses a cooling tower system, which includes:
3 ATC 800 cooling towers, with 22 kW fans and 5.5 kW pumps.
1 Tan Long cooling tower, with two 15 kW fans and two 3.7 kW pumps.
1 Tan Long cooling tower, with two 11 kW fans and two 3.7 kW pumps.
The fan motors are operated in an on-off automatic mode without variable frequency drive (VFD) control. There are several issues with the current operation of the cooling fans:
Frequent on-off cycling negatively impacts motor lifespan, as each start-up involves a large inrush current.
The on-off control method is not the most energy-efficient, and the control range is suboptimal.
Condenser system at the company

## Slide 25: EEMs 4: Installation of inverter for condenser cooling fan system
Solution: Install variable frequency drives (VFDs) for the cooling tower fans, using cooling water temperature signals to control the operation.
Energy Savings Calculation Summary:
Description | Unit | Value
Operating hours | hours/year | 8,448
Designed capacity | kW | 22
Operating capacity | kW | 18.50
Cooling fan system | Units | 3
Energy consumption | kWh/year | 468,864
Valve opening ratio | % | 90
Electricity price | VND/kWh | 1,692
Description | Unit | Unit | Value
New capacities | kW | kW | 16,04
Hours of operation after installation | Giờ/năm | Giờ/năm | 8 448
Electricity consumption | kW/năm | kW/năm | 406 467
Saving electricity | Units | Units | 63 397
Reduced Power | % | % | 13,31
Cost Savings |  |  | 
Savings |  | VND/kWh | 105.575.602
Equipment investment |  | VND | 114M
Labor |  | VND | 11.4M
Total investment |  | VND | 125,4M
Payback time |  | year | 1,2

## Slide 26: EEMs 5: Installing a Thermal Storage Tank for 10°C Chilled Water Supply to the Air Conditioning System
Current Status:
Vietnam Corporation is one of the units with high electricity consumption during peak hours. The cooling system for air conditioning and chilled water operates to provide 10°C chilled water to various areas through pumps, fans, and fan coil units (FCUs).
The demand for 10°C chilled water is high during peak hours, but the current system optimization is inefficient.
The operating period during peak hours is 5 hours, with electricity costs during peak hours being 2,871 VND, which is three times higher than off-peak costs (1,007 VND).

## Slide 27: EEMs 5: Installing a Thermal Storage Tank for 10°C Chilled Water Supply to the Air Conditioning System
Solution:
Install a thermal storage tank system to store cooling capacity during off-peak hours and release cooling during peak hours, thereby reducing operating costs of the cooling system.
Benefits of a Thermal Storage Tank:
A new technology, thermal storage tanks allow flexible energy management. They enable cooling production at the most convenient and cost-effective times while using the stored cooling capacity whenever needed.
Commonly used for storing cooling capacity for air conditioning systems in central cooling systems serving large buildings, supermarkets, the food industry, etc., utilizing electric-powered chillers.
Operating principle of cold storage tank system

## Slide 28: EEMs 5: Installing a Thermal Storage Tank for 10°C Chilled Water Supply to the Air Conditioning System
Two Basic Installation Modes:
1. Full Load Mode:
The thermal storage tank is charged with sufficient cooling capacity to meet peak demand. Chillers operate only at night to freeze water in the tank.
Advantages: Chillers do not operate during peak hours when electricity prices are highest.
2. Partial Load Mode:
Chillers are used to partially charge the thermal storage tank daily. Over 12 hours of operation, the tank supplies part of the cooling demand, while the chiller runs to provide the remaining capacity.

## Slide 29: EEMs 5: Installing a Thermal Storage Tank for 10°C Chilled Water Supply to the Air Conditioning System
Benefits: There are numerous advantages for investors, electricity suppliers, and the environment and society:
a. Benefits for investors:
Reduce costs by up to 40% by shifting the cooling demand to off-peak hours.
In partial storage mode, designers can reduce chiller size by approximately 50-60%, lowering installation costs.
Reduce the size and cost of air-handling equipment, motors, piping, and pumps by up to 30%.
Using a thermal storage tank reduces air humidity, allowing the thermostat to be set higher to achieve the same comfort level, thereby lowering operational costs.
Thermal storage tanks can be integrated into existing cooling systems, increasing cooling capacity while reducing operating costs.

## Slide 30: EEMs 5: Installing a Thermal Storage Tank for 10°C Chilled Water Supply to the Air Conditioning System
b. Benefits for Energy Providers:
Thermal storage tanks lower electricity demand during peak hours, improving the efficiency of electricity production for power plants.
Studies show that electricity is transmitted more efficiently during off-peak hours. Each kilowatt-hour of electricity shifted from peak to off-peak hours reduces the fuel required to generate it (by approximately 8–30%) and, correspondingly, reduces greenhouse gas emissions from power plants.
Decrease peak loads for electricity providers.

## Slide 31
c. Benefits for the Environment and Society:
Thermal storage tanks make energy storage for new energy sources (such as solar and wind) more feasible.
Reduce emissions and the use of polluting power plants by lowering peak loads.
Reduce the need for constructing additional power plants.
While there are many forms of energy storage, thermal storage tanks specifically reduce peak-hour energy demand and store energy for cooling purposes.
Using thermal storage tanks reduces the size of chillers, thereby decreasing the amount of refrigerant used and minimizing its leakage into the environment.
EEMs 5: Installing a Thermal Storage Tank for 10°C Chilled Water Supply to the Air Conditioning System

## Slide 32: EEMs 5: Installing a Thermal Storage Tank for 10°C Chilled Water Supply to the Air Conditioning System
d. Benefits for economy
No. | Item | Unit | Value
1 | Data Basis |  | 
1.1 | Motor capacity of high-efficiency screw compressor Mycom model N200LL | kW | 260
1.2 | Actual power consumption of the machine (Measured result from chiller No. 2) | kW | 182.50
1.3 | Cooling water pump capacity | kW | 7.5
1.4 | Cooling efficiency (estimated) | % | 90
1.5 | Calculation for 01 high-efficiency screw compressor Mycom | Unit | 1
No. | Item |  | Unit |  | Value
2 | Savings Calculation with the Addition of a Thermal Storage Tank |  |  |  | 
2.1 | Load shifting time (off-peak hours: 22h–4h) | Hours | Hours | 6 | 6
2.2 | Cooling time (peak hours: 9h30–11h30; 17h–20h) | Hours | Hours | 5 | 5
2.3 | Actual power consumption without a thermal storage tank (peak hours) | kW | kW | 855 | 855
2.4 | Electricity price during peak hours | VND/kW | VND/kW | 2,871 | 2,871
2.5 | Power costs during peak hours | VND | VND | 2,454,705 | 2,454,705
2.6 | Added pump capacity for thermal discharge | kW | kW | 5.5 | 5.5
2.7 | Actual power consumption with the addition of a thermal storage tank | kW | kW | 1,146 | 1,146
2.8 | Electricity price during off-peak hours | VND/kW | VND/kW | 1,361 | 1,361
2.9 | Power costs during off-peak hours | VND | VND | 1,559,706 | 1,559,706
Table 2: Savings Calculation with the Addition of a Thermal Storage Tank

## Slide 33: EEMs 5: Installing a Thermal Storage Tank for 10°C Chilled Water Supply to the Air Conditioning System
d. Benefits for economy
No. | Item | Unit | Value
3. Savings Potential |  |  | 
3.1 | Daily savings in power costs with a thermal storage tank | VND | 894,999
3.2 | Annual operating time | Days | 352
3.3 | Annual savings | VND | 315,039,648
3.4 | Investment cost | VND | 1,500,000,000
3.5 | Payback period | Years | 4.8
3.6 | Internal Rate of Return (IRR) | % | 1.7%
3.7 | Net Present Value (NPV) | Thousand VND | 65,003.484

## Slide 34: EEMs 6: Installing Energy Monitoring Meters
Current Situation
The company’s production process is divided into multiple stages, each with distinct characteristics, energy-consuming equipment, operating mechanisms, and varying durations.
The company needs to monitor energy usage, calculate energy consumption per unit of production monthly, and track energy losses in each area to identify causes and take timely corrective actions.
By installing sub-meters, the energy manager can establish monthly energy consumption benchmarks. These benchmarks will help monitor and analyze energy usage across different areas.

## Slide 35: EEMs 6: Installing Energy Monitoring Meters
Benefits
The energy manager can establish monthly energy consumption benchmarks by installing sub-meters. Using these benchmarks, they can calculate and prepare reports, generate charts, and compare monthly benchmarks to select the lowest energy consumption level as the target for the organization’s operations.
Monitoring energy usage and calculating energy consumption per unit of production monthly, along with tracking energy losses in each area, helps identify causes and address issues promptly.

## Slide 36: EEMs 6: Installing Energy Monitoring Meters
Day | EAC 1 |  |  | EAC 2 |  |  | EAC ... |  | 
 | Energy | Device Name | Consumption | Energy | Device Name | Consumption | Energy | Device Name | Consumption
1 |  |  |  |  |  |  |  |  | 
2 |  |  |  |  |  |  |  |  | 
3 |  |  |  |  |  |  |  |  | 
4 |  |  |  |  |  |  |  |  | 
5 |  |  |  |  |  |  |  |  | 
6 |  |  |  |  |  |  |  |  | 
... |  |  |  |  |  |  |  |  | 
30 |  |  |  |  |  |  |  |  | 
Sum |  |  |  |  |  |  |  |  | 
Energy consumption tracking form
Energy Monitoring Meter Used at the Company

## Slide 37
Dự án Thúc đẩy tiết kiệm năng lượng trong các ngành công nghiệp Việt Nam
THANK YOU