## Slide 1: TRAINING PROGRAME for IEs
The Vietnam Scaling up Energy Efficiency Project (VSUEE)
for: Enterprise leaders

## Slide 2: Training program for business leaders
TIME | Content
8.00 – 8.30 | Registration
8.30 – 8.40 | Opening Remarks
8.40 – 9.45 | Module 1: Project introduction Policy introduction: energy saving, greenhouse gas emission reduction, gender issues related in EE
9.45 – 10.00 | Breaks
10.00– 11.00 | Module 2. Relations between energy, environment and production and business, use of clean energy
11.00 – 11.45 | Module 3. The current situation of energy use and potential of industrial waste in Vietnam (cement, steel, seafood processing, brick and ceramic, textiles, beverages, paper and pulp, other industries (plastics...)
11.45 – 12.00 | Discuss
12.00 – 13.30 | Lunch
13.30 – 14.15 | Module 4. Energy Management, Energy Management System
14.15 – 15.00 | Module 5. EE project financing and VSUEE project financing approach
15.00 – 15.15 | Breaks
15.15 – 16.15 | Component 6. Case study in EE for Manufacturing Industry: Cement, Steel, Seafood Processing, Brick and Ceramic, Textile, Beverage, Paper & Pulp, Other Industries (Plastics...)
16.15 – 16.45 | Discuss
16.45 – 17.00 | Closing

## Slide 3
Module 6:
Typical report on energy efficiency in plastic industry in Vietnam
Dự án Thúc đẩy tiết kiệm năng lượng trong các ngành công nghiệp Việt Nam
TRAINING PROGRAME for IEs
for: Enterprise leaders

## Slide 4
Plastics Industry in Vietnam

## Slide 5: Content
Case study of typical facility Energy efficiency measures

## Slide 6
1
Case study of typical facility

## Slide 7: General Information
Main Production Field: Manufacturing products from plastic and synthetic rubber, copper hose valve fittings Main Products: PVC, PPR, HDPE Plastic Pipe, Copper Hose Valve Main energy equipment: substations, compressed air stations, circulation pumping stations...

## Slide 8: Production Line
Plastic pipe production process
Electricity
Mixing, feeding raw materials
Electricity
Electricity
Water
Electricity
Electricity
Electricity
Electricity
Electricity
Electricity
Refrigeration heating, mold
Extrusion Tube Forming
Vacuum,
cooling
Printing
Pipe Pulling
Pipe Cutting
Pipe Stretching, PVC Pipe Manufacturing
Pipe coil (HDPE pipe production
Product Quality Inspection
Enter storehouse
Pass
No- Pass
Chop, scrape spoiled
Shredding Scrap (PVC waste)
Granulation
(PPR & HDPE waste)
Compressed Air

## Slide 9: Production Line
Injection Molding Accessories Manufacturing Process
Electricity
Electricity
Electricity
Electricity
Mixing Raw Materials
Pellet Production (PVC Material)
Material Feeding
Compressed Air
Mold Changing and Technical Setting
Machine Heating
Injection Molding of Products
Quality Check of Products
Trimming & Packaging
Ware-house
Pass
Electricity
Water
Fail
Scrap Grinding

## Slide 10: Production Line
Faucet Valve Manufacturing Process
Input Materi-als
Cutting the billet
Hot Stamp- ing
Debur-ring
Polish-ing
Cut-ting
Finish-ing
Check
Ware-housing
Pass
Fail

## Slide 11: Production Line
Types of Energy Used in the Production Line:
Electricity is used in systems and equipment such as production lines, air conditioning, lighting, air compressors, etc.
The compressed air distribution system supplies compressed air to workshops. The compressed air system is responsible for providing compressed air to support the production processes throughout the company.
Diesel oil (DO) is used to meet production needs.
Water is used for both production and domestic purposes.

## Slide 12: Power Supply System
The company’s power supply is drawn from the 22 kV grid through 22kV/0.4kV transformers, which distribute electricity to various usage points.
Image of measuring equipment at the power station
The measurement and monitoring systems at the substations are relatively well-equipped. The company has installed both high-voltage and low-voltage power cos, ensuring that the power factor of the electrical supply system consistently remains above 0.9.
Substation pictures
1. Electrical System

## Slide 13: Power Supply System
The lighting system ensures that activities in the production area as well as the office area are stable and continuous. The lighting system at the company uses a system of LED bulbs of all kinds that are invested synchronously.
Some lighting locations of the factory
2. Lighting System

## Slide 14: Power Supply System
The company’s compressed air system consists of three compressed air stations:
Station 1 supplies compressed air to the Plastics Workshop,
Station 2 supplies compressed air to the Mechanical Workshop for valve and faucet production,
Station 3 – the air compressor is located in the Plastics Workshop.
The compressed air system is responsible for supplying compressed air to support the production processes across the entire company.
Hình ảnh trạm khí nén
3. Air compressor system

## Slide 15
2
Energy efficiency measures

## Slide 16: EEMs 1: Enhancing Internal Management and Equipment Maintenance
a. For the Electrical Equipment System:
Regularly promote and train employees on energy-saving practices. Increase the involvement of operating staff (energy-saving efforts must be widespread and supported by operational employees).
Monitor energy consumption based on production and non-production days to identify and address energy losses. Develop procedures and checklists to ensure that equipment is properly turned off when not in use.
Install automatic control devices to switch off equipment when not in use.
Turn off all unnecessary lighting (e.g., during break times, lunch hours, shift changes, or on days off).
Install compensation capacitors to create a “leading” power factor to address the “lagging” power factor of devices. These capacitors can be installed on individual devices or groups of devices to partially or fully manage the distribution system.
Control the ambient temperature to extend the insulation life and reliability of motors. Avoid exposing motors to direct sunlight, place them in well-ventilated areas, and keep them clean.

## Slide 17: EEMs 1: Enhancing Internal Management and Equipment Maintenance
b. For Refrigeration and Air Conditioning Systems
Regularly clean and replace filters, and clean evaporators and condenser coils to enhance the cooling efficiency of air conditioning units.
Set air conditioning systems to a reasonable temperature. The ideal temperature range is 26°C to 27°C during summer; it should not be set too low or too high. Setting the temperature too low causes the air conditioning system to operate for longer periods, increasing energy consumption. Lowering the temperature by just 1°C can increase energy consumption by 3-4%.
c. For Compressed Air Systems
Train and raise staff awareness to ensure efficient operation and maintenance of the compressed air system.
Ensure the system remains dry. Verify proper drainage slopes, discharge points, and outlets to limit pipe corrosion.
Invest in leak detection devices or air leak testing equipment to measure overall system losses and compressor capacity. Identify and repair compressed air leaks, and take preventive measures to avoid recurrence.

## Slide 18: EEMs 1: Enhancing Internal Management and Equipment Maintenance
d. For Office Buildings
Inspect the thickness of insulation layers on walls and roofs.
Review and seal any gaps to prevent heat loss from the room.
Use curtains on the inside and outside of windows to retain heat in winter and provide cooling in summer.
Install sunshades on windows to reduce heat during summer.
Install automatic door and gate closing devices.
Fit double-layer doors or air curtains for west-north facing areas.
Set air conditioning to above 26°C in summer and 23°C in winter.
Turn off all lighting equipment when not in use or at the end of work shifts.

## Slide 19: EEMs 2: Inspect, Monitor, and Address Compressed Air Leakage
Current Situation
Compressed air is utilized in factories for various processes, including production stages, valve control, mechanical systems, and other operations.
Over time, leaks often occur at quick connections and joints, resulting in compressed air loss. Significant leakage can impact production activities.
Based on the experience of auditing units, if compressed air leaks are not addressed, the amount of leakage can reach up to 10% of the total compressed air produced.

## Slide 20: EEMs 2: Inspect, Monitor, and Address Compressed Air Leakage
Solution
To improve the efficiency of compressed air usage, minimize air losses, and reduce energy consumption in the compressed air system, the company should implement the following measures:
Establish Operational Guidelines: Operators using compressed air should be required to immediately report any detected air leaks at their workstation to the technical team.
Introduce Penalties: Develop penalties for wasteful use of compressed air or failure to report detected leaks to the maintenance team, encouraging employees to take greater responsibility for the equipment they operate.
Regular Inspection Process: Implement a routine inspection process to identify and address compressed air leaks on a weekly basis.
Implementation Steps
Detection: Assign a dedicated team to use leak detection equipment to identify leaks throughout the company’s compressed air system. Locate and mark all leakage points in areas using compressed air.
Repair and Replacement: Address the identified leakage points by repairing or replacing faulty components.
Verification: Re-inspect the previously repaired or replaced points to ensure all leaks have been successfully resolved.

## Slide 21: EEMs 2: Inspect, Monitor, and Address Compressed Air Leakage
No. | Parameter | Unit | Value
1 | Average electricity price | VND | 1,860
2 | Average operating hours per day | Hours | 12
3 | Average operating days per year | Days | 312
4 | Number of leakage points | Points | 30
5 | Total leakage volume per year | m³/year | 305,286
6 | Electricity saved after implementing the solution | kWh/year | 36,634
7 | Income from energy savings in 1 year | Million VND | 68.1
8 | Investment cost for the solution | Million VND | 30
9 | Simple payback period | Months | 5
10 | CO2 emission reduction | Tons/year | 33.4

## Slide 22: EEMs 3: Improve the efficiency of air compressor operation and control
Current Status
The company operates two compressed air stations:
Station 1 supplies compressed air for the plastic product manufacturing workshop, equipped with three air compressors (two 55kW compressors and one 45kW compressor). Among these, one 55kW compressor and one 45kW compressor are integrated with inverters for compressor control.
Station 2 supplies compressed air for the mechanical workshop, comprising two 55kW compressors.
The compressed air system is used to produce and supply compressed air for controlling production equipment.

## Slide 23: EEMs 3: Improve the efficiency of air compressor operation and control
Solution
“Enhancing the operational efficiency and control of air compressors”
Based on the current state of the company’s compressed air system, the consulting team proposes the following efficiency improvement solutions:
Install a central control unit for Air Station 1 to maintain stable pressure and reduce compressor idle running time.
Install pipelines to exhaust hot air outside to improve the machine room environment and reduce the inlet air temperature for the compressors.
Adjust the set pressure to match the actual required pressure.
Minimize unnecessary compressed air usage, such as by closing air lines to unused machines, repairing leaks, and avoiding the use of compressed air for cleaning purposes.
Install and clean inlet air filters regularly to reduce intake resistance and improve compressor efficiency.

## Slide 24: EEMs 3: Improve the efficiency of air compressor operation and control
Compressed air station energy consumption according to the compressed air flow produced
Chart comparing the pressure fluctuations of an air compressor with an inverter compared to other air compressors

## Slide 25: EEMs 3: Improve the efficiency of air compressor operation and control
Function of the Compressed Air Station Controller
Automatically operates air compressors in the system according to the compressed air demand for production.
Configures compressor operation schedules to align with production times.
Synchronizes operating hours and start-up counts: ensures stable quality of supplied air and facilitates maintenance and servicing of the compressed air system.
Controller connection diagram in coordination with air compressors

## Slide 26: EEMs 3: Improve the efficiency of air compressor operation and control
No. | Parameter | Unit | Value
1 | Average electricity price | VND | 1,860
2 | Electricity saved after implementing the solution | kWh/year | 67,704
3 | Income from energy savings in 1 year | Million VND/year | 125.9
4 | Total investment cost for the project | Million VND | 200
5 | Simple payback period | Months | 19.1
6 | Discount rate | % | 10
7 | Project lifetime | Years | 10
8 | Project payback period | Tons/year | 21.4

## Slide 27: EEMs 4: Improving the Operational Efficiency of the Chiller System
Situation

## Slide 28: EEMs 4: Improving the Operational Efficiency of the Chiller System
Solution
Enhance the quality of makeup water: Use a chemical water softening system or an electrical water softening device.
Reduce scale buildup: Install electromagnetic descaling devices or rubber ball cleaning systems at the condenser and evaporator.
Regular maintenance: Perform maintenance on the chiller system 1-2 times per year to maintain operational efficiency.
Improving Cold Water Circulation System: Replace the underground cold water channel with elevated pipes (φ90-110mm), using two pumps with a power range of 11-15kW. Install a connected piping system and remove individual cold water pumps.

## Slide 29: EEMs 4: Improving the Operational Efficiency of the Chiller System
Solution
Convert to a closed-loop return water system: Use closed-loop pipes to prevent impurities and separate wastewater from being returned to the return tank.
Install automatic control valves: Control return water temperature and water levels in the tank, reduce heat loss, and prevent cold water from mixing with return water.
Renovate the storage tank: Add insulation to the cold water tank. Add partitions in the return water tank to settle dirt for easier cleaning.
Install interlock controllers: Synchronize the operation of the chiller, circulating cold water pumps, and the cooling tower fan system to reduce idle running time.

## Slide 30: EEMs 4: Improving the Operational Efficiency of the Chiller System
Solution
Optimize thermal efficiency: Ensure separation of lubrication oil and refrigerant. Increase the velocity of the secondary cooling fluid to an optimal level to avoid unnecessary energy consumption.
Clean heat exchange equipment: Remove scale from condenser tubes and evaporator equipment to reduce energy consumption (0.8mm scale buildup can increase energy consumption by 35%).
Cooling tower management: Select and maintain appropriately, reducing the water temperature from the cooling tower by 0.55°C to reduce energy consumption by 3%.

## Slide 31: EEMs 4: Improving the Operational Efficiency of the Chiller System
No. | Parameter | Unit | Value
1 | Average electricity price | VND | 1,860
2 | Electricity saved after implementing the solution | kWh/year | 705,510
3 | Income from energy savings in 1 year | Million VND/year | 1,312.2
4 | Total investment cost for the project | Million VND | 1,545
5 | Simple payback period | Months | 14.1
6 | Discount rate | % | 10
7 | Project lifetime | Years | 10
8 | Project payback period | Months | 15.7

## Slide 32: EEMs 5: Installation of Cold Storage System to Prevent Chiller System from Operating During Peak Hours
Current Situation
The chiller refrigeration system operates continuously to meet the actual load demand of the production workshops.
The total power of the chiller units when operating normally is about 150-250kW.
The electricity pricing follows a three-tier structure: peak hours, normal hours, and off-peak hours.
The electricity rates for the manufacturing sector in 2021 are as follows: Peak hours 2,871 VND/kWh, Normal hours 1,555 VND/kWh, Off-peak hours 1,007 VND/kWh. The peak-hour price is nearly three times the off-peak price.
Meanwhile, the chiller system operates 20-24 hours a day, with 3 out of 24 hours falling under peak hours (from 09:30 to 11:30 and from 17:00 to 18:00), leading to a high energy consumption rate for air conditioning.
Therefore, the energy cost for the air conditioning system during peak hours is also very high.

## Slide 33: EEMs 5: Installation of Cold Storage System to Prevent Chiller System from Operating During Peak Hours
Solution
Installing a cold storage system helps reduce electricity consumption costs for the chiller system. During off-peak hours, the chiller operates to cool the storage tank. This cold energy is then used during peak hours, reducing the load on the chiller and saving electricity costs.
a. Benefits for the Investor: Saves up to 40% in operating costs by shifting the cooling demand to off-peak hours. Reduces the size and installation costs of equipment (chiller, pipes, AHU). Increases efficiency and reduces air humidity, which lowers cooling load and costs. Can be integrated with the existing chiller system. | b. Benefits for the Electricity Supplier: Reduces peak load and increases electricity production efficiency. Reduces fuel demand and greenhouse gas emissions. Improves electricity transmission efficiency during off-peak hours. | c. Benefits for the Environment and Society: Reduces emissions, pollution, and the need to build additional power plants. Supports the storage of renewable energy (wind, solar). Reduces refrigerant leakage, protecting the environment.

## Slide 34: EEMs 5: Installation of Cold Storage System to Prevent Chiller System from Operating During Peak Hours
Solution
Operating Modes:
Full Load: The chiller operates only at night to completely cool the storage tank, without needing to operate during peak hours.
Partial Load: The tank provides part of the load, and the chiller continues to operate as needed.
This system is effective when the price difference between peak and off-peak electricity rates is significant, and it also helps increase the Coefficient of Performance (COP) due to lower ambient temperatures at night.

## Slide 35: EEMs 5: Installation of Cold Storage System to Prevent Chiller System from Operating During Peak Hours
No. | Item Description | Unit | Value
1. Database |  |  | 
1.1 | Total cooling capacity of Chiller (as per section 5.4.4) | kW (cooling) | 836
1.2 | Coefficient of Performance (COP) |  | 2.2
1.3 | Chiller efficiency |  | 0.85
1.4 | Utilization factor |  | 0.9
2. Calculation of thermal storage tank capacity |  |  | 
- | Load charging phase |  | 
2.1 | Off-peak load charging time | Hours | 6
2.5 | Total cooling capacity charged | kWh (cooling) | 3,837
2.6 | Cooling storage capacity of thermal storage medium | kWh/m³ | 120
2.7 | Required volume of thermal storage medium | m³ | 32

## Slide 36: EEMs 5: Installation of Cold Storage System to Prevent Chiller System from Operating During Peak Hours
No. | Item | Unit | Value
- | Cooling Discharge Phase |  | 
2.8 | Energy loss from cold storage tank | % | 10
2.9 | Available cooling capacity | kWh (cooling) | 3,454
2.10 | Total discharge time | hours | 6
2.11 | Design capacity of the heat exchanger used | kW (cooling) | 640
2.12 | Converted electricity during discharge time | kWh | 1,570
2.13 | Electricity price during peak hours | VND/kWh | 2,871
2.14 | Electricity price during normal hours | VND/kWh | 1,555
2.15 | Electricity consumption during peak hours | kWh/day | 1,900
2.16 | Electricity consumption during normal hours | kWh/day | 380
2.17 | Electricity cost during peak hours per day | VND/day | 6,045,800

## Slide 37: EEMs 5: Installation of Cold Storage System to Prevent Chiller System from Operating During Peak Hours
No. | Item | Unit | Value
3. Calculation of energy used for cold storage |  |  | 
3.1 | Electricity consumption during off-peak hours (6 hours) | kWh/day | 2,280
3.2 | Electricity price during off-peak hours | VND/kWh | 1,007
3.3 | Electricity cost for off-peak cold storage | VND | 2,295,960
4. Savings Potential |  |  | 
4.1 | Energy loss during the cold storage process | kWh | 174
4.2 | Electricity cost savings using the cold storage tank in 1 day | VND/day | 3,749,840
4.3 | Usage time | days/year | 312
4.4 | Annual cost savings | million VND | 1,170.0
4.5 | Investment cost | million VND | 3,837
4.6 | Simple payback period | months | 39.4
4.7 | Project lifespan | months | 120

## Slide 38: EEMs 6: Improvement of EE for Injection Molding Machines
Current Situation
Currently, the company uses multiple hydraulic pump motors in the plastic factory, primarily for injection molding machines. The hydraulic pump system consists of:
Hydraulic pump motor
Hydraulic pump
Pressure oil tank
Oil pipes
Valve system, piston, cylinder, and control mechanism
The motors operate in a Load & Unload mode, with a significant amount of idle time (e.g., the push mechanism for the mold has 70-80% idle time). Since the fixed pumps continuously provide maximum flow, excess oil is returned through a relief valve to the tank, resulting in energy waste and oil heating. Additionally, the oil pumps are designed for the highest load, but the actual power demand is rarely fully utilized, leading to low energy efficiency.

## Slide 39: EEMs 6: Improvement of EE for Injection Molding Machines
Solution
Operating Principle
The variable frequency drive (VFD) receives pressure/flow signals from the system to adjust the hydraulic pump motor speed accordingly:
When the pressure/flow is high, the motor speed increases to meet the demand.
When the pressure/flow is low, the motor speed decreases, saving energy.
Advantages
The VFD, combined with intelligent control, adjusts the motor speed based on pressure and flow signals, shifting from fixed-speed operation to variable-speed operation. This enhances motor efficiency and reduces energy consumption.

## Slide 40: EEMs 6: Improvement of EE for Injection Molding Machines
Effectiveness
• Closed-loop control optimizes power consumption.
• Saves 25-40% of the energy consumed by the hydraulic pump motor.
P, Q
P, Q (Áp suất, lưu lượng)
Technology diagram
Connection diagram of the control section when installing the inverter

## Slide 41: EEMs 6: Improvement of EE for Injection Molding Machines
No. | Parameter | Unit | Value
1 | Average electricity price | VND | 1,657
2 | Electricity saved after implementing the solution | kWh/year | 238,680
3 | Revenue from energy savings in 1 year | Million VND/year | 444
4 | Total investment cost for project implementation | Million VND | 1,800
5 | Simple payback period | months | 48.7
6 | Project lifecycle | years | 10
7 | Project payback period | months | 33.5

## Slide 42: EEMs 7: Installation of Solar Power System on Factory Rooftop
Current Status:
Hung Yen is located in the northern region, characterized by a tropical monsoon climate with hot summers, heavy rainfall, and cold winters with little rain. This region receives abundant solar radiation, high temperatures, and is suitable for solar power systems.
The average number of sunlight hours is about 1,600 hours per year, with solar radiation intensity ranging from 3.3 to 4.1 kWh/day. The highest radiation occurs in June (4.67 kWh/m²/day), and the lowest during the winter. These conditions make the solar power system efficient and help extend the lifespan of the equipment.
The factory in Hung Yen has a large, unobstructed roof, making it ideal for solar panel installation and energy absorption. The system is also easily relocatable if necessary.

## Slide 43: EEMs 7: Installation of Solar Power System on Factory Rooftop
Solution:
With the current situation as above, the proposed solution is: "Installing a rooftop solar power system in the factory". Below are the parameters of the roof area of the workshops and the capacity of the battery system that can be installed:
Image of the installation location of the solar power system
Installation Location | Total roof area (m2) | Usable area for installation (m2) | Solar Power System Installation (kW)
Factory roof | 39.000 | 20.000 | 2000

## Slide 44: EEMs 7: Installation of Solar Power System on Factory Rooftop
Operating Principle:
Principle diagram of rooftop solar power system

## Slide 45: EEMs 7: Installation of Solar Power System on Factory Rooftop
Benefits:
Reduces energy costs, especially during peak hours (9 AM - 12 PM), helping to save on monthly electricity bills and reduce grid load during the dry season.
High durability, long warranty, and low maintenance costs.
Simple system, easy to operate, upgrade, and expand.
Independent of fuel, avoiding the impact of rising fuel prices.
Enhances aesthetics and modernity, adding prestige to the building or company.
Utilizes clean, renewable, sustainable solar energy, protecting the environment and reducing greenhouse gas emissions.
Contributes to reducing global warming, acid rain, smog, and improving the green, quiet, odorless environment without the need for additional fuel.

## Slide 46: EEMs 7: Installation of Solar Power System on Factory Rooftop
No. | Parameter | Unit | Value
1 | Average electricity price during the day | VND | 1,943
2 | Annual electricity consumption | kWh/year | 9,108,710
3 | Number of sunlight hours in a year | Hours | 1,600
4 | Investment rate | Million VND/kWp | 15
5 | Electricity generated by solar panels in a year | kWh/year | 3,200,000
6 | Solar power proportion compared to the factory's annual electricity consumption | % | 35.1
7 | Total investment cost for implementing the solution | Million VND | 30,000
8 | Revenue from the solar panel system in a year | Million VND/year | 6,218
9 | Simple payback period | Months | 57.9
10 | CO2 emission reduction | Tons/year | 2,922

## Slide 47
Dự án Thúc đẩy tiết kiệm năng lượng trong các ngành công nghiệp Việt Nam
THANK YOU