## Slide 1
VIETNAM SCALING UP ENERGY EFFICIENCY PROJECT
(VSUEE)

## Slide 2
TECHNICAL APPRAISAL, INCLUDING TECHNICAL RISK MITIGATION

## Slide 3
Case studies and discussions
4
Guidance on preparing project appraisal reports
3
Calculation and appraisal of energy savings
2
TABLE OF CONTENT
Technical assessment for energy efficiency sub-projects
1

## Slide 4
Technical assessment for energy efficiency sub-projects

## Slide 5
General Introduction:
Assessing the validity of loan applications from IEs (Industrial Enterprises) for funding energy efficiency (EE) sub-projects is a critical responsibility of PFIs (Participating Financial Institutions), aimed at confirming that the selected sub-projects are financially and technically feasible. To support PFIs and IEs in conducting technical assessments for EE projects, the Technical Assessment Framework provided in Appendix 2 of the Project’s OM (Operations Manual) is used. (Download the VEEIE Project OM from: http://cpee.vn/VEECIES)
This Technical Assessment Framework will be used by PFIs to evaluate each sub-project considered for EE lending. The framework defines the content, sequence, and responsibilities for conducting technical assessments of sub-projects to ensure: (1) Industrial EE projects comply with Vietnam’s technical and sectoral regulations and policies; (2) Building EE projects comply with or exceed Vietnam’s construction codes.
Technical assessment for energy efficiency sub-projects

## Slide 6
(3) The project fully meets the technical eligibility criteria:
Clearly define and delineate the technical and physical boundaries and components of the sub-project within the overall production system or building of the borrowing enterprise;
Confirm whether the sub-project investment is limited to the renovation and restoration of existing physical components and systems;
Confirm that the energy-saving payback period for the sub-project investment is less than 10 years, based on the cash flow benefits derived from the energy savings achieved by the sub-project.
The energy-saving payback period will be calculated as follows:
Energy-saving payback period = Total investment cost of the sub-project / Average annual cash flow from energy savings.
(4) The project is technically feasible, safe, and efficient, contributing to enhanced energy savings and energy efficiency implementation.
Technical assessment for energy efficiency sub-projects

## Slide 7
In addition:
(5) Review and assess the technical capacity of the design, construction, installation units, equipment manufacturers, etc., where appropriate;
(6) Evaluate and compare the system design solutions, key technology and process options, and equipment choices presented in the feasibility study report; verify the reasons for selecting the system design, technology, processes, and equipment; assess the compatibility of the technology with existing systems; review and verify changes in specifications and indicators (of technology, processes, equipment, systems, products, production capacity) before and after the sub-project;
(7) Review and validate the baseline energy efficiency (before the sub-project) and the consumption scenario within the boundaries of the sub-project;
Technical assessment for energy efficiency sub-projects

## Slide 8
(8) Identify and validate the overall improvements in energy efficiency and energy savings resulting from the sub-project, as well as the key components of energy efficiency improvements and energy savings in terms of technology, processes, and equipment;
(9) Review and validate technical risks and risk mitigation measures;
(10) Review and validate the technical feasibility of the implementation plan;
(11) Review and validate the estimated investment cost of the sub-project (including analysis of cost components).
(12) Review the completeness of legal documents in the project dossier (Environmental License, Fire Prevention & Fighting Certificate, Product Certification, and other relevant legal approvals). If any legal requirements for credit/investment arise, these must be documented and recommended in the appraisal report to ensure overall compliance.
Technical assessment for energy efficiency sub-projects

## Slide 9
During the appraisal process, the PFI will conduct a technical assessment of the sub-project. Upon receiving the relevant documents from the IE, the PFI will perform the technical assessment of the sub-project with the support of a technical expert, an energy audit expert, and an environmental expert. These experts must have experience relevant to the specific type of project: Industrial Sub-projects, ESCO Sub-projects, or Building Sub-projects.
If the PFI lacks any of the required experts, it will hire external consultants with appropriate technical expertise and experience to conduct the technical assessment. The technical experts will also participate in and contribute to the financial analysis, as well as sub-project monitoring and reporting.
The technical assessment will be carried out by reviewing the feasibility study report, energy audit report, other relevant documents, as well as through field visits and interviews. The findings of the technical assessment will be included in the appraisal report.
Technical assessment for energy efficiency sub-projects

## Slide 10
Technical assessment for energy efficiency sub-projects
(6) Legal and permitting requirements
  (1) General description of the scope of the sub-project and the end-borrowing enterprise.
  (2) Project objectives and justification.
  (3) Summary of the technical assessment of the sub-project
  (4) Baseline energy consumption data and the sub-project's projected energy savings.
(5) Social and environmental assessment.
(7) Total investment estimate and financial plan
Evaluation Process and Procedures:
Potential IEs (Industrial Enterprises) seeking funding for energy efficiency (EE) sub-projects must submit a Loan Application File to the PFI (Participating Financial Institution). In addition to the PFI’s standard information requirements for loan applications, the loan application file for an EE sub-project must include the following information:
Notes: Environmental and Social Assessment: This section serves to meet the environmental and social safety standards required by international financiers (e.g., the IFC Performance Standards). → This typically does not require a full Environmental Impact Assessment (EIA) Report, but rather an evaluation of key risks and impacts.
Legal and Permitting Requirements: This section must comply with the regulations of Vietnamese law and state management agencies, including: EIA, Fire Prevention and Fighting, Labor Safety, Epidemiological Hygiene, etc.

## Slide 11
The PFI will conduct an initial review of the loan application file. To review the energy efficiency project loan application, the PFI's review team must include an energy efficiency expert responsible for detailed technical review and measurement and verification (M&V) of energy savings, as well as an environmental expert.
In addition to other documents required by the PFI at the time of loan application, it is recommended that the IE submit official copies of the following:
(1) Feasibility study of the sub-project,
(2) Government approval for project implementation (if required),
(3) Government environmental approval, and
(4) Other relevant documents such as baseline energy audit reports.
Technical assessment for energy efficiency sub-projects

## Slide 12
If the final version of the sub-project feasibility study is not yet available, the IE may submit a reasonably developed draft at the time of loan application. However, the IE must provide the official version of the feasibility study before the Preliminary Appraisal begins.
The PFI's project team will conduct an initial review of the loan application file and discuss with the IE to assess whether the sub-project complies with eligibility criteria and meets the PFI's policy and credit requirements.
Technical assessment for energy efficiency sub-projects

## Slide 13
Feasibility Study of the Sub-Project:
The IE is responsible for preparing the feasibility study report for the sub-project to submit to the PFI. The IE shall submit a draft or official version of the feasibility study report along with the loan application documents. The IE must submit the final version of the feasibility study report to the PFI before or during the Preliminary Appraisal stage.
The sub-project feasibility study report must include:
(1) Assessment of the technical feasibility of the sub-project
(2) Technical implementation plan
(3) Investment cost estimate and cost details
(4) Baseline energy audit study before sub-project implementation and projected energy savings
(5) Environmental impact assessment of the sub-project and mitigation measures (if required)
These components of the feasibility study may be presented in the form of one or several reports and may be conducted by one or multiple parties.
Technical assessment for energy efficiency sub-projects

## Slide 14
(1) Assessment of the Technical Feasibility of the Sub-project
- Analysis of the rationale and benefits of the energy efficiency sub-project
- Assessment of technical retrofitting and restoration, including:
Evaluation and comparison of system design options
Assessment of key process and technology alternatives
Review of equipment choices
- Evaluation of the reliability, efficiency, and compatibility of the new system's design, technology, processes, equipment, and products with the existing system
- Assessment of anticipated changes in technical requirements and indicators (e.g., technology, processes, equipment, systems, products, production capacity) before and after the project
- Technical evaluation criteria for energy efficiency sub-projects: Examples of evaluation criteria are presented in the following slide.
Technical assessment for energy efficiency sub-projects

## Slide 15
Evaluation criteria:
(1) Amount of energy saved (%)
(2) Impact on equipment lifespan and durability
(3) Compatibility of equipment within the entire system
(4) Impact on maintenance costs
(5) Impact on business operations
(6) Requirements for worker operating skills and work attitudes
(7) Equipment installation space
(8) Aesthetics
(9) ….
Technical assessment for energy efficiency sub-projects

## Slide 16
Technical Evaluation Table (Example)
Technical assessment for energy efficiency sub-projects
Criteria | Option 1 | Option 2 | Option 3
(1) Energy savings (%) |  |  | 
(2) Impact on machinery lifespan and durability |  |  | 
(3) Compatibility of equipment within the entire system |  |  | 
(4) Impact on maintenance costs |  |  | 
(5) Impact on business operations |  |  | 
(6) Requirements for operational skills and worker attitude |  |  | 
(7) Equipment installation space |  |  | 
(8) Aesthetics |  |  | 
(9) … |  |  | 

## Slide 17
(2) Technical implementation plan
(3) Investment cost estimate and cost details
Implementation plan for the sub-project and the various parties expected to participate in the sub-project implementation;
Analysis of limitations and challenges for implementation and recommended mitigation measures.
Analysis of equipment, installation, and consulting costs related to the sub-project, serving as the basis for cost estimation.
Assessment of the total investment amount, including interest during construction and contingency costs.
Technical assessment for energy efficiency sub-projects

## Slide 18
Research and analyze the energy usage of the beneficiary enterprise or relevant party, the plant, or the area of the beneficiary enterprise where the sub-project will be implemented to establish baseline energy consumption data.
Baseline data must include data on all forms of energy consumed over a one-year period, preferably for the two most recent years. In addition to the volume of energy consumed, the average expenditure during that period for each energy form should also be calculated. Energy consumption for all energy forms after project implementation and the assumptions used as the basis for estimation must also be detailed.
Evaluation of the measurement and verification plan to ensure compliance with widely accepted M&V (Monitoring and Verification) methods.
(4) Baseline energy audit study before sub-project implementation and expected energy savings
(5) Environmental impact assessment of the sub-project and mitigation measures (if required).
Technical assessment for energy efficiency sub-projects

## Slide 19
Calculation and appraisal of energy savings

## Slide 20
Calculation and appraisal of energy savings
Energy conversion factor |  |  |  | 
No. | Fuel Type | Unit | TOE/Unit | Note
1 | Electricity | kWh | 0.0001543 | 
2 | Coke | Ton | 0.70 - 0.75 | 0.725
3 | Coal type 1,2 | Ton | 0.7 | 
4 | Coal type 3,4 | Ton | 0.6 | 
5 | Coal type 5,6 | Ton | 0.5 | 
6 | DO (Diesel Oil) | Ton | 1.02 | 
 |  | 1000 Liters | 0.88 | 
7 | FO (Fuel Oil) | Ton | 0.99 | 
 |  | 1000 Liters | 0.94 | 
8 | LPG | Ton | 1.09 | 
9 | Natural Gas | Thousand m³ | 900 | 
10 | Gasoline (for cars and motorcycles) | Ton | 1.05 | 
 |  | 1000 Liters | 0.83 | 
11 | Jet Fuel | Ton | 1.05 | 
(Source: Ministry of Industry and Trade - attached to Document No. 3505/BCT-KHCN dated April 19, 2011)
Note:
TOE - Ton of Oil Equivalent Emission Factor (tCO₂/MWh) 0.8154
(According to Document No. 315/KTTVBĐKH-GSPT dated March 17, 2017, by the Department of Meteorology, Hydrology and Climate Change regarding the emission factor for Vietnam's grid electricity in 2015)

## Slide 21
I. Borrower's energy consumption BEFORE energy efficiency investment |  |  |  | 
1. Annual Electricity Consumption |  |  |  | 
Electricity Consumption | MWh / year |  |  | 
2. Annual Fuel Consumption |  | Total Consumption | Conversion Factor to kWh | Consumption in MWh
Natural Gas | Thousand Liters / year |  | 5,832.79 | -
Heavy Fuel Oil | Ton/ year |  | 6,610.50 | -
Light Fuel Oil | Thousand Liters / year |  | 6,092.03 | -
Liquefied Petroleum Gas (LPG) | kg / year |  | 7.06 | -
Diesel | Thousand Liters / year |  | 5,703.18 | -
Gasoline | Thousand Liters / year |  | 5,379.13 | -
Coke | Ton/ year |  | 4,698.64 | -
Coal type 1,2 | Ton/ year |  | 4,536.62 | -
Coal type 3,4 | Ton/ year |  | 3,888.53 | -
Coal type 5,6 | Ton/ year |  | 3,240.44 | -
Other Fuels: [specify] | [Enter unit] |  |  | 
Total Energy Consumption in MWh / year (Abefore) |  |  |  | -
Calculation and appraisal of energy savings

## Slide 22
Calculation and appraisal of energy savings
I. Borrower's energy consumption AFTER energy efficiency investment |  |  |  | 
1. Annual electricity consumption |  |  |  | 
Electricity Consumption | MWh / year |  |  | 
2. Annual Fuel Consumption |  | Total consumption | Conversion factor to kWh | Consumption in MWh
Natural Gas | Thousand Liters / year |  | 5,832.79 | -
Heavy Fuel Oil | Ton/ year |  | 6,610.50 | -
Light Fuel Oil | Thousand Liters / year |  | 6,092.03 | -
Liquefied Petroleum Gas (LPG) | kg / year |  | 7.06 | -
Diesel | Thousand Liters / year |  | 5,703.18 | -
Gasoline | Thousand Liters / year |  | 5,379.13 | -
Coke | Ton/ year |  | 4,698.64 | -
Coal type 1,2 | Ton/ year |  | 4,536.62 | -
Coal type 3,4 | Ton/ year |  | 3,888.53 | -
Coal type 5,6 | Ton/ year |  | 3,240.44 | -
Other Fuels: [specify] | [Enter unit] |  |  | 
Total energy consumption in MWh / year (Abefore) |  |  |  | -

## Slide 23
III. ANNUAL ENERGY SAVINGS |  |  |  |  |  |  | 
1. Annual Electricity Consumption |  |  |  |  |  |  | 
Electricity consumption |  | MWh / year |  |  |  |  | -
2. Annual fuel savings |  |  |  | Total savings |  | Conversion factor to kwh | Savings in MWh
Natural Gas |  | Thousand m³ / year |  | - |  | 5,832.79 | -
Heavy Fuel Oil |  | Ton / year |  | - |  | 6,610.50 | -
Light Fuel Oil |  | Thousand Liters / year |  | - |  | 6,092.03 | -
Liquefied Petroleum Gas (LPG) |  | kg / year |  | - |  | 7.06 | -
Diesel |  | Thousand Liters / year |  | - |  | 5,703.18 | -
Gasoline |  | Thousand Liters / year |  | - |  | 5,379.13 | -
Coke |  | Ton / year |  | - |  | 4,698.64 | -
Coal type 1,2 |  | Ton / year |  | - |  | 4,536.62 | -
Coal type 3,4 |  | Ton / year |  | - |  | 3,888.53 | -
Coal type 5,6 |  | Ton / year |  | - |  | 3,240.44 | -
Gasoline |  | Thousand Liters / year |  |  |  |  | 
Total energy savings in MWh / year (DA = Atrước x Pa/Pb - Asau) |  |  |  |  |  |  | -
Total annual energy savings as a percentage ( = (DA x 100) / (Atrước x Pa/Pb)) (%) |  |  |  |  |  |  | #DIV/0!
Annual CO2 reduction in tons |  |  |  |  |  |  | -
Where |  |  |  |  |  |  | 
- Annual production (output) expected after the sub-project (Pa): |  |  |  |  |  |  | 1.00
- Average annual production (output) of the 2 years before the sub-project (Pb): |  |  |  |  |  |  | 1.00
- Production coefficient (= Pa / Pb) |  |  |  |  |  |  | 1.00
Calculation and appraisal of energy savings

## Slide 24
Guidance on preparing project appraisal reports

## Slide 25
Below is the guidance prepared to support the Appraisal Team in developing the Appraisal Report:
Description of the Borrower
Type of borrower (e.g., Industrial Enterprise (IE), ESCOs, building owners, and end-users from municipal governments)
Industrial Enterprise (IE):
General introduction of the IE: Year of establishment, charter capital, scale of operations, position in the industry, etc.
Organizational and management structure of the IE: Organizational chart, list of Board of Directors and senior executive committee, financial and information management, etc.
Relationship between the borrower (IE) and PFI: Previous loans, debt repayment, current credit limits, relationship with other financial institutions.
ESCOs:
General introduction of the borrower: Year of establishment, charter capital, scale of operations, position in the ESCO sector, etc.
Guidance on preparing project appraisal reports

## Slide 26
      Organizational and Management Structure of the Borrower: Organizational chart, list of Board of Directors and senior executive committee, financial and information management, etc.
      Relationship between the Borrower and PFI: Previous loans, debt repayment, current credit limits, relationship with other financial institutions.
      Description of the Investment Recipient Enterprise: Type of enterprise, year of establishment, charter capital, organizational and management structure.
      Building owner/end-user/building heating & cooling system operator:
      Borrower (building owner, school/hospital, heating or cooling system operator)
      Description of (the) project equipment
      Construction date
      Location: Address and description of the surrounding area (e.g., building type—residential, commercial, or government administrative buildings)
      Organizational and management structure of the borrower, including the Board of Directors and/or management framework.
      Relationship between the borrower and PFI: Previous loans, debt repayment, current credit limits, relationship with other financial institutions.
Guidance on preparing project appraisal reports

## Slide 27
II. Business operations of the borrower and financial assessment
1. For industrial enterprise borrowers
  Assessment of the borrower's industrial indicators, trends, prospects, and market position; evaluation of the borrower's management strengths and corporate governance structure; analysis of key business risks.
  Analysis of state policies and guidelines for the industry, and PFI's policies and guidelines for the industry.
  Financial status of the borrower: Based on a comprehensive analysis of the borrower's financial reports—capital structure, operating profit, sales growth, debt repayment capacity, liquidity, etc.
Guidance on preparing project appraisal reports

## Slide 28
2. For ESCO borrowers
Assessment of the borrower's market position, customer base, prior experience, past performance in ESCO projects, evaluation of management strengths and corporate governance structure; analysis of key business risks.
Review of state policies and guidelines for the ESCO sector, and PFI's policies and guidelines for this sector.
Financial status of the borrower: Based on a comprehensive analysis of the borrower's financial reports—capital structure, operating profit, sales growth, debt repayment capacity, liquidity, etc.
Audited financial statements for the past 3 years.
Prior project experience (in tabular form on the following slide):
  Experience in implementing similar projects.
  Performance results of those projects.
  References for those projects.
Guidance on preparing project appraisal reports

## Slide 29
INFORMATION ON ESCO'S PAST PERFORMANCE
Guidance on preparing project appraisal reports
End-User Contact Information | 
Equipment Type | 
Installation Year | 
Project Brief Description | 
Installed Technology | 
Total Implementation Cost | 
Total Loan Amount | 
Lender Name | 
Loan Tenure | 
Expected Energy Savings/Year | 
Actual Energy Savings/Year | 
Measurement Method | 
Energy Cost Savings/Year | 
Other Cost Savings/Year | 
Total Cost Savings/Year | 
Savings Share for ESCO (%) | 
Expected Cash Flow to ESCO/Year | 
Actual Cash Flow to ESCO/Year | 
Loan Repayment/Year | 
Cash Flow to Debt Service Ratio | 
Contract Performance Period | 

## Slide 30
3. For building owner borrowers
Assessment of the borrower's key industry indicators, trends, prospects, and market position; evaluation of the borrower's management strengths and corporate governance structure; analysis of key business risks.
Analysis of state policies and guidelines for the industry, and PFI's policies and guidelines for the industry.
Financial status of the borrower: Based on a comprehensive analysis of the borrower's financial reports—capital structure, operating profit, sales growth, debt repayment capacity, liquidity, etc.
Borrower's experience in similar projects:
  Equipment type
  Brief description
  Installed technology
  Implementation cost
  Achieved savings
Guidance on preparing project appraisal reports

## Slide 31
III. Sub-project Description
1. For all borrowers
- Description of the proposed project,
- Summary of the sub-project investment cost, financing plan, and proposed sub-loan amount
- List of the sub-project's Energy Efficiency Measures (EEMs) - using the template in the following table:
SUB-PROJECT'S ENERGY EFFICIENCY MEASURES (EEMs)
No. | Description | Technology Used | Investment Cost | % Savings | Energy Savings | Cost Savings | Simple Payback Period
1 |  |  |  |  |  |  | 
2 |  |  |  |  |  |  | 
3 |  |  |  |  |  |  | 
4 |  |  |  |  |  |  | 
5 |  |  |  |  |  |  | 
Total | - | - |  | - |  |  | 
Guidance on preparing project appraisal reports

## Slide 32
Copy of the Feasibility Study Report, Information on the capacity of the entity conducting the Feasibility Study; and
If required, Baseline Energy Audit, Information on the capacity and certifications of the energy auditor, and Information on the audit standards used by the energy auditor when conducting the Baseline Energy Audit.
Audit Grade Requirement: The Energy Audit Report must achieve Investment Grade Audit (IGA) level.
Data Validation: Cost information and equipment performance data in the audit report must be based on supplier quotations/specifications, accompanied by source references (quotations, catalogues, datasheets).
2. Additional information required for ESCO borrowers
Copy of the Energy Performance Contract between the ESCO and the end-user
Description of key contract terms:
  Description of performance/energy savings guarantees provided
  Description of provisions on savings sharing
  Description of the measurement and verification methods for performance and savings
Identification of subcontractors, including Design-Procurement-Construction partners, and a summary of their energy-related experience with similar projects
Description of the subcontractor selection method used
Guidance on preparing project appraisal reports

## Slide 33
Information about the end-user:
  Type of business
  Years in operation
  Audited financial statements for the last 3 years
  Detailed review conducted by the ESCO
  Explanation of why the ESCO believes the end-user will remain operational during the loan tenure.
IV. Technical assessment of the sub-project
Based on the feasibility study of the sub-project prepared by the borrower
Review of the sub-project, including details of the restoration, renovation, technology to be used, implementation capacity, sub-project location, description of sub-project equipment, expected output, and implementation schedule
Evaluation of the rationale for the chosen design/technical approach; verification of the reliability and effectiveness of the technology, and its performance in other projects
Assessment of the expected technical performance and energy savings, and analysis of the projected energy savings from the sub-project
Confirmation of compliance with valid technical criteria
Guidance on preparing project appraisal reports

## Slide 34
V. Financial Assessment of the Sub-project
1. For All Borrowers
  Financial feasibility analysis of the sub-project - calculation of the Financial Internal Rate of Return (FIRR) for the investment.
  Analysis of the impact on the borrower's profitability, cash flow, and balance sheet.
2. Additional Assessment for ESCO Borrowers
  Analysis of the impact on the end-user's net cash flow and profitability over the entire sub-loan tenure.
  Total cost including interest during construction.
  Terms of the performance contract: Debt repayment, sharing of energy savings between the ESCO and the end-user; ESCO's cash flow.
  Level of energy savings guarantee and the method of securing such guarantees.
Guidance on preparing project appraisal reports

## Slide 35
      Expected Energy Savings and Energy Cost Savings - By Year
      Expected Other Cost Savings - By Year
      Total Expected Cost Savings - By Year
      Savings Share for ESCO - By Year
      Savings Share for End-User - By Year
      Debt Amount
      Debt Service Cost - By Year
      M&V Cost - By Year
      Total Cost Savings to Debt Service Ratio - By Year
      ESCO's Cost Savings to Debt Service Ratio - By Year
      Proposed Measurement and Verification (M&V) Method
Guidance on preparing project appraisal reports

## Slide 36
VI. Costs, Financing Plan, and Debt Repayment of the Sub-project
Detailed breakdown of sub-project costs by component, separated into foreign currency and VND costs with appropriate pricing and physical contingencies, working capital requirements, and interest costs during the construction period.
Includes bases and assumptions for cost estimation (feasibility study, supplier budgets/quotes, baseline estimation date, etc.).
Analysis of funding sources for the sub-project, including the value of financing and reliability of funds from each source.
PFI's contribution to the total required sub-loan amount for the sub-project.
Analysis of the legitimacy of the loan purposes and its underlying information, including the legitimacy of the loan type, purpose, compliance status, and its basis; and
Analysis of the repayment plan, sources, and risks:
Expected monthly savings
Expected monthly debt repayment and loan tenure
Monthly debt service to monthly savings ratio
Sustainability of the recipient enterprise: Whether it will remain operational in its sector
Guidance on preparing project appraisal reports

## Slide 37
VII. Collateral and guarantee analysis
Analysis of the guarantor, including their operations, financial status, and creditworthiness;
Analysis of collateral/pledged assets, including baseline records, legality, validity, appraisal value, and calculation of collateral/pledged assets;
For ESCO projects, analysis of the Energy Performance Contract between the ESCO and the end-user, expected savings, and the Measurement and Verification (M&V) methods used to verify performance and ensure sustainability;
PFI's contribution to the total required sub-loan amount for the sub-project.
VIII. Environmental impact assessment and resettlement policy framework evaluation
Description of the environmental and social impacts of the sub-project and the required or anticipated mitigation measures;
Confirmation of required government approvals, environmental categorization, Environmental Impact Assessment (if required);
Confirmation of compliance with valid environmental criteria;
Confirmation of whether the Resettlement Policy Framework is triggered for the proposed sub-project.
Guidance on preparing project appraisal reports

## Slide 38
Confirmation of the types of resettlement instruments required to develop the Resettlement Policy Framework (RPF) for the proposed sub-project;
Confirmation of compliance with required government approvals for recent land acquisition and that the Resettlement Action Plan (RAP) meets the requirements of the RPF for proposed land acquisition activities in the sub-project.
IX. Procurement and Bidding
Description of the main procurement packages for goods, along with an evaluation of contractual arrangements, methods, and potential suppliers;
Description of imported equipment: reasons for importing equipment, performance characteristics of the imported equipment;
Commercial contract: supplier, commercial value, contract terms, payment methods and conditions;
Confirmation that the loan will be disbursed in accordance with the procurement framework.
X. Conclusion
Proposed borrower credit rating;
Proposed terms of the sub-loan: loan amount, interest rate;
Internal discussion issues.
Guidance on preparing project appraisal reports

## Slide 39
Case studies and discussions

## Slide 40
Case studies and discussions
Case of the steel rolling plant:
Current energy consumption status
Month | Electricity consumption in 2024 | 
 | Electricity Consumed (kWh) | Cost (VND)
1 | 1 098 001 | 1 084 442 307
2 | 542 890 | 523 738 148
3 | 1 045 813 | 1 059 734 539
4 | 814 809 | 825 320 207
5 | 1 216 108 | 1 216 254 184
6 | 1 175 712 | 1 185 327 376
7 | 1 056 811 | 1 070 734 553
8 | 859 386 | 887 543 666
9 | 1 046 300 | 1 067 404 100
10 | 844 800 | 876 300 300
11 | 1 182 000 | 1 238 661 000
12 | 1 069 200 | 1 075 321 000
Total |  | 

## Slide 41
Case studies and discussions
Case of the Steel Rolling Plant:
List of major electricity-consuming equipment
Lighting Equipment |  |  |  |  |  | 
No. | Type of high-pressure lamp | Power (kw) | Quantity | Operating time (h/day) | Location | 
1 | High-Pressure Lamp | 250W | 16 | 12 | Around the Workshop | 
2 | High-Pressure Lamp | 250W | 30 | 12 | Pipe Finishing Section | 
3 | High-Pressure Lamp | 250W | 12 | 12 | Pipe Rolling Section | 
4 | High-Pressure Lamp | 250W | 150 | 4 | Other Sections | 
5 | Fluorescent Tube | 40W | 56 | 16 | Pipe Rolling Section | 
6 | Fluorescent Tube | 40W | 52 | 8 | Other Sections | 
7 | Fluorescent Tube | 20W | 32 | 8 | Office | 
Pumps and Fans Equipment |  |  |  |  |  | 
No. | Equipment | Quantity | Power (kW) | Operating time (h/day) | Condition | Location
1 | Single-Phase Industrial Fan | 9 | 0.19 | 5 | Normal | Metal Processing Section
2 | Single-Phase Industrial Fan | 9 | 0.19 | 10 | Normal | Pipe Rolling Section
3 | Three-Phase Water Cooling Fan | 1 | 7.5 | 8 | Normal | Steel Rolling Section

## Slide 42
Case studies and discussions
Case of the steel rolling plant:
List of major electricity-consuming equipment
4 | Single-Phase Industrial Fan | 6 | 0,19 | 10h | BT | Steel Rolling Section
5 | Three-Phase Water Cooling Fan | 1 | 0,63 | 8h | BT | Pressing Section
6 | Three-Phase Water Cooling Fan | 3 | 0,21 | 8h | BT | Pressing Section
7 | Single-Phase Industrial Fan | 10 | 0,19 | 7h | BT | Pressing Section
8 | Three-Phase Industrial Exhaust Fan | 6 | 2,11 | 16h | BT | Pipe Finishing Section
9 | Three-Phase Water Cooling Fan | 1 | 3,5 | 8h | BT | Pipe Finishing Section
10 | Three-Phase Water Cooling Fan | 1 | 5 | 8h | BT | Pipe Finishing Section
11 | Single-Phase Industrial Fan | 9 | 0,19 | 10h | BT | Pipe Finishing Section
12 | Single-Phase Industrial Fan | 4 | 0,2 | 8h | BT | Cutting Section
13 | Three-Phase Industrial Exhaust Fan | 4 | 2,42 | 10h | BT | Sink Finishing Section
14 | Single-Phase Industrial Fan | 9 | 0,25 | 7h | BT | Sink Finishing Section

## Slide 43
Case studies and discussions
Case of the steel rolling plant:
List of major electricity-consuming equipment
15 | Single-Phase Industrial Fan | 7 | 0,21 | 8h | BT | Energy Workshop
16 | Single-Phase Industrial Fan | 2 | 0,19 | 7h | BT | Electromechanical Section
17 | Single-Phase Industrial Fan | 4 | 0,21 | 6h | BT | Pipe Warehouse
18 | Single-Phase Water Pump | 3 | 0.21 | 16h | BT | Sink Finishing Section
19 | Three-Phase Water Pump | 3 | 5.27 | 24h | BT | Steel Rolling Section
20 | Three-Phase Water Pump | 1 | 8.42 | 24h | BT | Steel Rolling Section
21 | Single-Phase Water Pump | 3 | 1.37 | 24h | BT | Pressing Section
22 | Three-Phase Water Pump | 1 | 1.37 | 16h | BT | Pipe Finishing Section
23 | Three-Phase Water Pump | 4 | 5.27 | 16h | BT | Pipe Finishing Section
24 | Three-Phase Water Pump | 3 | 3.42 | 16h | BT | Pipe Finishing Section
25 | Single-Phase Water Pump | 1 | 0.53 | 8h | BT | Pipe Finishing Section
26 | Three-Phase Water Pump | 2 | 2.37 | 24h | BT | Pipe Finishing Section
27 | Three-Phase Water Pump | 1 | 5.27 | 24h | BT | Electromechanical Section

## Slide 44
Case studies and discussions
Case of the steel rolling plant:
List of major electricity-consuming equipment
Air Compressors |  |  |  |  |  | 
No. | Type of Air Compressor | Quantity | Power (KW) | Operating time (hour/day) | Condition | Location
1 | Screw Air Compressor | 2 | 75 | 24h | Normal | Electromechanical Section
2 | Air Dryer | 2 | 1.58 | 24h | Normal | Electromechanical Section
Electrical Equipment in Production Line |  |  |  |  |  | 
No. | Type of Motor | Quantity | Power (KW) | Operating time (hour/day) | Condition | Location
1 | DC Motor | 2 | 167 | 16 | Normal | Steel Rolling Section
2 | DC Motor | 2 | 124 | 16 | Normal | Steel Rolling Section
3 | DC Motor | 2 | 263 | 16 | Normal | Steel Rolling Section
 | Three-Phase Motor | 4 | 8.42 | 16 | Normal | Pipe Finishing Section
4 | Three-Phase Motor | 88 | 2.75 | 24h | Normal | Pipe Finishing Section
5 | Three-Phase Motor | 30 | 3.42 | 24h | Normal | Pipe Finishing Section
6 | Three-Phase Motor | 40 | 1.1 | 3h | Normal | Pipe Finishing Section
7 | Three-Phase Motor | 51 | 2.63 | 16 | Normal | Pipe Rolling Section
8 | Three-Phase Motor | 52 | 2.85 | 16 | Normal | Pipe Rolling Section
9 | Three-Phase Motor | 17 | 3.42 | 16 | Normal | Pipe Rolling Section
10 | Three-Phase Motor | 8 | 5.27 | 16 | Normal | Pipe Rolling Section

## Slide 45
Case studies and discussions
Case of the steel rolling plant:
List of major electricity-consuming equipment
No. | Equipment Type | Quantity | Power (KW) | Operating Time (h/day) | Condition | Location
11 | Three-Phase Motor | 4 | 8.42 | 16 | Normal | Pipe Rolling Section
12 | Three-Phase Motor | 2 | 13.69 | 8 | Normal | Pipe Rolling Section
13 | DC Motor | 10 | 8.42 | 24 | Normal | Pipe Rolling Section
14 | DC Motor | 2 | 18.75 | 16 | Normal | Pipe Rolling Section
15 | Three-Phase Motor | 58 | 0.25 | 16 | Normal | Pipe Rolling Section
16 | DC Motor | 1 | 105.72 | 8 | Normal | Cutting Section
17 | DC Motor | 1 | 160.75 | 8 | Normal | Cutting Section
18 | Three-Phase Motor | 3 | 8.42 | 8 | Normal | Cutting Section
19 | 10-ton Crane | 2 | 10 | 6 | Normal | Cutting Section
20 | 10-ton Crane | 1 | 10 | 6 | Normal | Cutting Section
21 | 20-ton Crane | 1 | 21 | 5 | Normal | Cutting Section
22 | 5-ton Crane (Single-Phase) | 1 | 7.37 | 4 | Normal | Pressing Section
23 | 5-ton Crane (Single-Phase) | 1 | 7.37 | 5 | Normal | Cutting Section

## Slide 46
Case studies and discussions
Case of the steel rolling plant:
List of major electricity-consuming equipment
No. | Equipment Name | Quantity | Power (KW) | Operating Time (h/day) | Condition | Location
24 | 5-ton Hong Nam Crane | 1 | 8 | 6 | Normal | Pipe Rolling Section
25 | 3.2-ton Crane | 4 | 4.21 | 8 | Normal | Pipe Finishing Section
26 | 3.2-ton Crane | 3 | 4.21 | 8 | Normal | Pipe Rolling Section
27 | 3.2-ton Crane | 1 | 4.21 | 4 | Normal | Energy Workshop
28 | 3.2-ton Crane | 3 | 4.21 | 7 | Normal | Pipe Warehouse
29 | 3.2-ton Crane | 1 | 4.21 | 3 | Normal | Semi-finished Product Warehouse
30 | 2-ton Crane | 2 | 3.5 | 3 | Normal | Decorative Pipe Storage
31 | 600mm Width Annealing Furnace (Furnace 1,2) | 2 | 272.48 | 24 | Normal | Steel Rolling Section
32 | 500mm Width Annealing Furnace (Furnace) | 1 | 266.55 | 24 | Normal | Steel Rolling Section
33 | 500kVA Pipe Annealing Furnace | 1 | 258.0 | 8 | Normal | Pipe Finishing Section
34 | 350kVA Pipe Annealing Furnace | 1 | 170.5 | 7 | Normal | Pipe Finishing Section
35 | 300kVA Pipe Annealing Furnace | 1 | 152.69 | 7 | Normal | Pipe Finishing Section
36 | 200-ton Hydraulic Press 1 | 1 | 30 | 7 | Normal | Pressing Section
37 | 200-ton Hydraulic Press 2 | 1 | 30 | 7 | Normal | Pressing Section

## Slide 47
Case studies and discussions
Case of the steel rolling plant:
List of major electricity-consuming equipment
No. | Equipment Name | Quantity | Power (KW) | Operating Time (h/day) | Condition | Location
38 | 200-ton Hydraulic Press 3 | 1 | 30 | 10 | Normal | Pressing Section
39 | 400-ton Hydraulic Press 1 | 1 | 55 | 7 | Normal | Pressing Section
40 | 400-ton Hydraulic Press 2 | 1 | 55 | 10 | Normal | Pressing Section
41 | 680-ton Hydraulic Press 1 | 1 | 75 | 10 | Normal | Pressing Section
42 | 680-ton Hydraulic Press 2 | 1 | 75 | 10 | Normal | Pressing Section
43 | Band Saw Machine | 3 | 0.19 | 7 | Normal | Pipe Rolling Section
44 | Lathe Machine | 2 | 1.58 | 7 | Normal | Electromechanical Section
45 | Milling Machine | 1 | 1.4 | 4 | Normal | Electromechanical Section
46 | Punching Machine | 4 | 01.05 | 8 | Normal | Energy Workshop
47 | Punching Machine | 3 | 2.37 | 8 | Normal | Pressing Section
48 | Plasma Welding Machine | 4 | 11.85 | 16 | Normal | Pipe Rolling Section
49 | Plasma Welding Machine | 3 | 4.74 | 16 | Normal | Pipe Rolling Section

## Slide 48
Case studies and discussions
Case of the Steel Rolling Mill:
List of potential energy saving opportunities
No. | Opportunity | Estimated Saving Potential, % | Notes
1 | Enhanced in-house management | 2 ÷ 5 | Compared to the plant's electricity consumption
2 | Lighting system retrofit | 25 | Compared to the pre-retrofit system
3 | Install inverters for air compressors | 20 ÷ 25% | Compared to the equipment's consumption before installation
4 | Install Powerboss devices for stamping presses | 15 ÷ 25% | Compared to the equipment's electricity consumption before installation
5 | Insulation for 02 600-width annealing furnaces | 10 ÷ 15% | Compared to the equipment's electricity consumption before installation

## Slide 49
Case studies and discussions
Case of the steel rolling plant:
Analysis of the current situation and proposed energy efficiency solutions
Renovation of the lighting system
Current Status: The factory has a large workshop area equipped with numerous machinery and equipment requiring different operational needs, leading to highly diverse lighting requirements. As the lighting needs vary for each area, the factory's lighting system is decentralized and inconsistent. The factory makes relatively good use of natural lighting. However, due to the high ceiling of the workshop, the illumination level on cloudy days or during night shifts is insufficient. The current workshop lighting primarily only ensures basic visibility for movement. Equipment and areas requiring high illumination still rely on localized lighting.
The workshops still use approximately 258 250W high-pressure mercury vapor lamps and a number of 40W magnetic ballast fluorescent lamps.

## Slide 50
Case studies and discussions
Case of the steel rolling plant:
Analysis of the current situation and proposed energy efficiency solutions
Lighting system retrofit
Solution: Replace 258 mercury high-pressure lamps (250W) with equivalent brightness sodium high-pressure lamps (150W), and replace 110 magnetic ballast fluorescent lamps (40W) with electronic ballast fluorescent lamps (32W).
During the installation of the new lighting system, attention should be paid to:
Segmenting lighting circuits and arranging switches in convenient locations to control lighting in work areas, ensuring both technological lighting requirements in workshops and energy efficiency.
Lowering the height of high-pressure lamps to a reasonable level. Adjust the lamp height according to the lighting area to improve lighting quality.
Enhancing lighting in areas requiring high illumination and optimizing switch arrangements to minimize unnecessary lighting.

## Slide 51
Case studies and discussions
Case of the steel rolling plant:
Analysis of current status and proposed energy efficiency measures
Install Inverter for 01 Air Compressor
Current Status: The plant currently operates two 75 kW air compressors in parallel to supply compressed air for technological equipment. These compressors have significant idle cycles, accounting for 20-40% of operation time. Both compressors operate simultaneously:
When system pressure < 0.6 MPa, both compressors run under load.
When system pressure > 0.7 MPa, both compressors enter idle mode (no air supply to the system, motors still running, compressed air bypassed back to the compressors).
Solution: Optimize the operation of the compressed air production and distribution system.
Repair compressed air leaks at usage points, air valves, and compressed air pipelines (reduce demand-side load).
Use one compressor for base load and the other for peak load. Install an inverter on the peak-load compressor to optimally control the motor speed, ensuring sufficient air supply for demand. Regularly alternate the roles of the two compressors to ensure continuous operation and even wear.

## Slide 52
Case studies and discussions
Case of the steel rolling plant:
Analysis of current status and proposed energy efficiency measures

## Slide 53
Case studies and discussions
Case of the steel rolling plant:
Analysis of current status and proposed energy efficiency measures
Image of the factory's stamping press and annealing furnace

## Slide 54
Case studies and discussions
Case of the steel rolling plant:
Analysis of current status and proposed energy efficiency measures
Insulating the annealing furnace
Current status: The survey revealed that the two 600-width belt annealing furnaces experience significant heat loss to the environment. The external wall temperatures on both sides of the furnaces range from 70°C to 100°C, with some areas near the resistor wire installation points and furnace entry/exit doors reaching 100°C to 150°C. The average ambient temperature around the furnaces is approximately 80°C. The dimensions of these two furnaces are: Length: 9.5 m × Width: 1.90 m × Height: 1.78 m.
Proposed solution: Add an additional insulation layer to the two external walls of the furnaces to reduce heat loss to the environment. This will help stabilize the internal temperature, minimize heat dissipation, and reduce the furnaces' electricity consumption.
However, the solution faces several challenges:
The furnaces have multiple power supply points on both side walls, and the resistor wires have limited length.
Adding an insulation layer may alter the furnace structure (based on expert feedback).
While the solution could yield significant energy savings, its feasibility is relatively low.
The business should carefully evaluate and decide on implementation. Nevertheless, insulating the two gable ends of the furnaces is unaffected by these challenges and should be implemented immediately to minimize heat loss through these areas.

## Slide 55
Case studies and discussions
Case of the steel rolling plant:
Analysis of current status and proposed energy efficiency measures
Installing power factor correction capacitors near major electrical equipment
Current Status: The company has installed power factor correction capacitor cabinets at the electrical substations to meet the requirements of the power utility. However, the electrical equipment within the company is distributed across a wide area, with many devices located far from the power supply sources. According to the survey, the power factor (cosφ) of the equipment typically ranges from 0.4 to 0.8, which is relatively low. Therefore, installing capacitor cabinets only at the substation primarily serves to compensate for reactive power to comply with the utility’s requirements.
Proposed Solution: Install power factor correction capacitors at distribution cabinets near major electrical equipment. This approach will reduce electrical losses in the transmission lines from the substation to the equipment, improve energy efficiency, and optimize the power factor locally.

## Slide 56
Case studies and discussions
Case of the steel rolling plant:
SUMMARY TABLE OF ENERGY SAVING OPPORTUNITIES
No. | Description | Technology Used | Investment Cost (Million VND) | Energy Saving (%) | Energy Savings (MWh/year) | Cost Savings (Million VND/year) | CO₂ Emission Reduction (tons/year) | Simple Payback Period (months) | Lifespan (years)
1 | In-house Management | - | - | 2.5% | 300 | 330 | 123.90 | - | -
3 | Lighting System | Retrofit, bulb replacement | 83.85 | 40% | 59.60 | 57 | 24.61 | 17.8 | 5
4 | 75kW Air Compressor | Install VSD | 165.00 | 20% | 104.74 | 115 | 43.26 | 17.2 | 10
5 | 680T Stamping Press (2 units) | Install Powerboss | 187.20 | 25% | 57.75 | 64 | 23.85 | 35.4 | 10
6 | 400T Stamping Press (2 units) | Install Powerboss | 128.70 | 22% | 53.72 | 59 | 22.19 | 26.1 | 10
7 | 200T Stamping Press (3 units) | Install Powerboss | 123.00 | 22% | 27.44 | 30 | 11.33 | 48.8 | 10
8 | 600-Width Annealing Furnaces (2 units) | Insulation retrofitting | 83.90 | 5.61% | 242.27 | 267 | 110.06 | 3.8 | 4
9 | Install Capacitors at F16 Cabinet | Install capacitors | 18.00 | 33.33% | 9.90 | 11 | 04.09 | 19.8 | 10
 | Total |  | 789.65 |  | 855.42 | 933 | 363 |  | 

## Slide 57
Case studies and discussions
Other cases and discussions:
Page 56

## Slide 58
Thank you!