## Slide 1
VIETNAM SCALING UP ENERGY EFFICIENCY PROJECT (VSUEE)

## Slide 2
Measurement and Verification (M&V)

## Slide 3
M&V
THE NATURE & BENEFITS OF M&V
M&V PLANNING
SIMULATION CALCULATION PRACTICE
Common Issues in M&V

## Slide 4
INTRODUCTION M&V

## Slide 5
What is M&V?
Measurement & Verification
The process of using measurement data to reliably determine the amount of energy saved in a building after implementing energy-saving measures.
  Measurement
  Data collection
Measurement
  Determining the amount of energy saved
Verification

## Slide 6
DIFFERENTIATING M&V AND MONITORING
Criteria | M&V (Measurement & Verification) | Monitoring (System Monitoring)
Primary Purpose | Calculate & verify energy savings after implementing ECM | Monitoring and controlling system operations
Legal & Financial | Used in EPC contracts, carbon credits, ISO 50001 certification, etc. | Not directly used for verifying savings or payments
Usage data | May come from actual measurements, operational records, or monitoring systems | Real-time data from sensors, meters, BMS/EMS
Adjustment factors | Adjusted for operating conditions (output, weather, etc.) | No adjustment, raw data
Savings calculation | Yes (Baseline – Use ± Adjustments) | No (only monitors real-time consumption values)
Timing of implementation | Before and after ECM, periodically | Frequently, continuously
Applicable standards | IPMVP, ISO 50015, ASHRAE Guideline 14… | Not required by M&amp;V standards

## Slide 7
WHY IS M&V NECESSARY?
1. Facilitate sustainability
Understand the reality of savings, adjust operations accordingly
Maintain & enhance long-term savings
Good M&V programs =&gt; higher, more sustainable savings
2. Financial support & investment risk reduction
M&A builds trust for banks, investment funds, and lenders
Facilitates the development of off-balance-sheet financial models
Provides a guarantee basis for debt repayment cash flow
3. Promotes better system design techniques
M&V design requires a thorough understanding of the production system-> contributes to improving design quality
Promote system design that is both technically efficient and operational.
4. Verifying and selling carbon credits (emission reductions)
M&V helps demonstrate CO2 reduction
As a basis for obtaining carbon credits (CDM, VCS, ETS, Mechanisms 6.2 – 6.4
5. Enhancing Transparency & Public Disclosure
Enhances credibility and public support for the project
Useful for sustainability reporting, meeting environmental standards: LEED, GRI, ISO 50001
6. Support national strategies & policies
Tool for facilitating international commitments on climate change

## Slide 8
THE ROLE OF M&V WITH STAKEHOLDERS
1. Investor/Project Owner
2. ESCO/Service Provider
Verifying whether a project is truly cost-effective
Settlement basis with EPC or ESCO contractors
Optimizing system operation and maintenance
Financial risk management
Demonstrating the technical effectiveness of energy conservation measures (ECM)
Revenue calculation based on performance contracts
Enhance credibility and create transparency with customers and financers

## Slide 9
THE ROLE OF M&V WITH RELATED PARTIES
3. Financial institution/Investor
Implementing off-balance sheet financing models
Limiting project financing risks

## Slide 10
SOME CONCEPTS
Baseline period
A specific period of time used as a reference for comparison with the reporting period
Energy baseline
Quantitative standards established as a basis for comparing energy efficiency
Energy Performance Improvement Action (EPIA)
Actions/measures implemented/planned to achieve energy efficiency improvements
Energy consumption
The amount of energy used
Energy efficiency
Measurable results related to energy performance, energy use, and energy consumption
Energy Performance Index (EnPI)
Quantitative value or measure of energy efficiency, as determined by the organization

## Slide 11
METHOD FOR ESTABLISHING A BASELINE
Historical data
  Use electricity/fuel bills or actual measurement data prior to the project
  Data must represent normal operating conditions
Regression statistics
  Use energy data & independent variables (e.g., weather, production) to build a regression model
System modeling
  Applicable when operating conditions change significantly
  Use multivariate linear regression analysis to relate energy to variables: temperature, production, etc.
Energy simulation
  Used for new projects or projects without historical data
  Use software: eQuest, EnergyPlus to simulate the baseline assumption

## Slide 12
OPERATING CONDITIONS
Concept:
Factors that directly affect energy consumption in facilities/equipment, apart from the impact of energy conservation measures (ECMs)
If these conditions change between the "before" and "after" implementation of ECMs
            Adjust the Baseline or Measured Use to determine the actual savings.
Download usage
Weather/Environment
Production/Production Activities
Maintenance level
Operating Procedures

## Slide 13
ENERGY SAVINGS
Energy Savings – The amount of energy no longer needed after implementing energy conservation measures (ECM) compared to previous consumption under equivalent conditions
Energy Savings = Ebaseline − Ereporting ± adjustments
Ebaseline: Energy used during the pre-improvement phase
Ereporting: energy measured after improvement
Δ adjustments: adjustments due to changes in operating conditions

## Slide 15
ENERGY SAVINGS
Detailed example:
The factory replaces high-efficiency motors:
Factors | Value
Electricity consumption before improvement (Baseline) | 120,000 kWh/year
Post-improvement consumption | 95,000 kWh/year
10% increase in production → adjustment + 10,000 kWh | (+) 10,000 kWh
⇨ Actual savings = 120,000 – 95,000 + 10,000 = 35,000 kWh/year

## Slide 16
THE ROLE OF ADJUSTMENTS

## Slide 18
Routine Adjustments (Routine Adjustments) | Non-Routine Adjustments (Non-routine adjustments)
•Used for predictable effects of changes in the post-retrofit phase (weather, number of people, production, etc.) •Quantitatively related to energy usage •4 Basic Options for implementing this adjustment •Baseline Adjustments | •For changes whose effects are unpredictable but significantly impact energy consumption •Based on actual changes and agreed upon at the site •Baseline Adjustments

## Slide 20
MEASUREMENT ERROR & UNCERTAINTY
MEASUREMENT ERROR
The deviation between the measured value and the actual value
Depends on the measuring device, installation method, and measurement environment
UNCERTAINTY
A measure of the reliability of energy-saving results
Includes random and systematic errors, affecting the accuracy of M&V reports

## Slide 21
MEASUREMENT ERROR & UNCERTAINTY
Accuracy of measuring devices
Electricity meter
Current Transformer (CT)
Temperature sensor
Air/water flow sensor
Importance in finance
If the error is large 🡪 the sponsor does not trust 🡪 the project is difficult to borrow capital
High uncertainty 🡪 unacceptable risk in programs

## Slide 22
PLANNING M&V

## Slide 23
M&V PLAN
Purpose: A foundation for determining accurate and verifiable savings.
Ensure all necessary data is available & budget control.
1
ECM Description
2
Define the measurement boundaries for savings
3
Documentation of the base year
4
Define post-retrofit phase &amp; adjustment
5
Describe design intent & commissioning process
6
Specify measurement options
7
Describe the data analysis process and algorithms
8
Defining measurement points, measurement times, and measurement device characteristics

## Slide 24
M&V PLAN
Purpose: A foundation for determining accurate and verifiable savings.
Ensure all necessary data is available & budget control.
9
For Option A: specify the assumed value &amp; impact
10
Option D: name of simulation software, input/output data
11
Quality Assurance (QA) process
12
Expected accuracy & qualitative impact
13
Method of reporting results, sample illustration
14
Third-party verification possible
15
If future changes can be predicted, determine baseline
16
Budget estimate, required resources

## Slide 25
ENERGY CONSUMPTION MEASUREMENT TECHNOLOGY
Energy consumption can be determined by
  Electricity or fuel bills, data from the main meter
  Separate measurement devices for retrofitted areas/equipment, capable of measuring in short cycles or continuously
  Separate measurement of parameters: power, operating time =&gt; total energy consumption
  Calibrated computer simulation
  Agreed-upon assumptions (stipulations) for high-reliability ECM parameters
The use of assumptions instead of actual measurements must be based on:
  The scope of identified savings
  Responsibilities among parties
  The potential impact of assumed errors

## Slide 26
INTRODUCTION TO 4 M&V OPTIONS (OPTION A-B-C-D)
Criteria | Option A Partial measurement – Improved isolation | Option B Full measurement – Improved isolation | Option C Entire system | Option D Simulation
 | Partially Measured Retrofit Isolation | Retrofit Isolation | Whole Facility | Calibrated Simulation
Measurement Range | Partial parameters Remaining Assumptions | Measure all parameters related to ECM | Measure total NL for the entire project | Simulation using software
Accuracy | Average Depends on assumptions | High | Dependent on the quality of the regression model | High if the model is correct
Cost | Low | Moderate to high | Low (invoice processing) | High (software, accurate data)
*Source: IPMVP

## Slide 27
INTRODUCTION TO 4 M&V OPTIONS (OPTION A-B-C-D)
Criteria | Option A Partial measurement – Improved isolation | Option B Full measurement – Improved isolation | Option C Entire system | Option D Simulation
Typical application | Lighting, small pumps | HVAC, motors, fans, chillers | Buildings, factories, shopping malls | Projects without historical data
Data requirements | Continuous short-term measurement combined with assumed values | Continuous short-term measurement | Analysis of main or secondary meter data | Energy usage simulation, calibrated using billing data
Adjustment analysis | Manual or simple | May require a small model | Requires statistical regression | Based on model assumptions
*Source: IPMVP

## Slide 29
PRACTICAL CALCULATIONS

## Slide 30
OPTION A – PARTIAL MEASUREMENT – IMPROVED ISOLATION
Illustrative example
Replace a 40W fluorescent bulb with a 20W LED bulb
Assumption: 10 hours of use per day. 300 days per year
Measurement: Electricity consumption rate of 1 light bulb
Calculation method:
Savings = (40W – 20W) x 10h x 300 days = 60,000 Wh = 60 kWh/year/bulb
Advantages | Limitations
Cost-effective, easy to implement Suitable for large numbers of identical devices | Average accuracy Not suitable if the operating load varies significantly or there are many influencing factors.

## Slide 31
OPTION B – FULL MEASUREMENT - IMPROVED ISOLATION
Illustrative example
The company replaced the old water pump with a high-efficiency motor integrated with a variable speed drive (VSD)
Actual measurement data
Before retrofit:
      Average measured power: 10.5 kW
      Operating time: 16 hours/day
      Recorded over 7 consecutive days
    After retrofitting
      Average measured power: 6.8 kW
      Constant operating time: 16 hours/day
      Recorded over 7 consecutive days
Calculation method:
Savings (kWh) = (10.5 kW – 6.8 kW) x 16 x 30 x 365 = 21,608 kWh/year

## Slide 32
OPTION C – ENTIRE FACILITY
Illustrative example
A 6-story office building implements multiple energy conservation measures (ECMs)
Replacing all lighting in the building with LEDs
Optimizing the HVAC system with BMS
Installing variable frequency drives for water pumps & AHU fans
Energy savings assessment based on the building's total electricity bill
Electricity bill data
Month | Pre-improvement consumption (2023) | Post-improvement consumption (2024) | Average temperature
January | 120,000 kWh | 105,000 kWh | 20.0 °C
February | 115,000 kWh | 97,000 kWh | 22.0°C
March | 125,000 kWh | 109,000 kWh | 26.5°C

## Slide 33
OPTION C – ENTIRE FACILITY
❶ Monthly electricity savings
Month | Electricity savings (kWh)
Month 1 | 120,000 – 105,000 = 15,000
February | 115,000 – 97,000 = 18,000
March | 125,000 – 109,000 = 16,000
Total savings for 3 months = 15,000 + 18,000 + 16,000 = 49,000 kWh
❷ Estimated financial savings
Assuming average electricity price: 2,000 VND/kWh
3-month savings = 49,000 x 2,000 = 98,000 VND

## Slide 34
OPTION D – STANDARD EFFECT SIMULATION
Illustrative example
A new data center built in 2024, featuring energy conservation measures (ECMs)
Installation of a high-efficiency cooling system (inverter chiller)
Well-insulated enclosure design (walls, roof)
LED lighting system and sensor calibration
New construction, no baseline data available

## Slide 35
OPTION D – SIMULATION OF STANDARD EFFECT
❷ Compare simulation results &amp; actual results
Data | Value
Floor area | 5,000 m²
Design simulation model | Prediction: 720,000 kWh/year
Actual meter reading data | Recorded: 765,000 kWh/year
Simulation climate data | TMY weather file for Hanoi
Actual weather in 2024 | Slightly different from TMY (with 5 unusually hot days)
③ Estimated savings
Building model without ECM: 880,000 kWh/year
Model with ECM (calibrated): 720,000 kWh/year
Savings = 160,000 kWh/year
❶ Use energy simulation software (EnergyPlus, eQuest, IESVE, DOE-2)

## Slide 36
COMMON ISSUES

## Slide 37
COMMON ISSUES
Factors affecting energy efficiency
  Many factors affect equipment performance &amp; savings levels
  Predictable and measurable factors can be used for routine adjustments
  Unmeasurable, unpredictable factors cause fluctuations and must be addressed through extraordinary adjustments
Assessing the uncertainty of savings
  Arising from: measurement device errors, model errors, sampling errors, regulatory assumptions
  Quantifiable factors should be quantified, and non-quantifiable factors should be qualitatively assessed
  Uncertainty can be reduced by using measured data and increasing sample size
Minimum energy performance standards
  If there are regulations or internal standards, the baseline can be set using this minimum standard

## Slide 38
COMMON ISSUES
Minimum operating conditions
  The ECM shall not be degraded in operating conditions without the user's consent
  The operating conditions to be maintained must be clearly stated in the M&V Plan
Energy pricing
  Prices are applied from the energy price list or marginal price, taking into account all factors on the bill
  M&V contract should specify the price at which cost savings will be calculated - generally iyt is the baseline price (pre-installation)
Third-party verification
  An independent third party may assist the investor in verifying the M&V plan and savings report
  May be experienced but not yet licensed

## Slide 39
COMMON ISSUES
Data for the emissions trading program
  Basis for verifying savings in the emissions trading program
  Need to separate electricity savings by season, peak/off-peak hours, and fuel type if different EFs apply
Adjustment of the non-routine baseline
  Applicable when unexpected changes occur: increase in area, equipment changes, operational targets
  Requires a method to track changes
Weather data & costs
  Prioritize government-published data, on-site data
  Costs depend on ECM complexity, number of measurement points, independent variables, and measurement time