## Slide 1
Module 15:
Preliminary energy audit

## Slide 2: CONTENT
1
Overview of EE
Preliminary EE
2
2

## Slide 3: 1.1. Objectives of energy audit levels
Implementing Initial Objectives
For ESCOs: Screening Potential Clients
Developing an EE Project Based on Economic and Technical Criteria
Investment Objectives
Ensuring Stakeholder Consensus on Action
  Understand the impact of the current situation and the potential for improvement
  Assess the feasibility of solutions
  Reduce investment risk
  Maximize economic return on investment
Objective of enterprise
Energy Audit – Possible Results

## Slide 4: 1.1. Objectives of energy audit levels
Objective of enterprise
Cash outflows
Energy, operation saving
Cash outflows
Implementation time
Construction time
Marketing,
audit
Time brings efficiency
Operations, Energy, M&V, Debt Services
Cash inflows
Project life circle

## Slide 5: 1.1. Objectives of energy audit levels
Objective of enterprise
Optimize Audit & M&V Costs
=
More Net Benefit for Clients!
Net Benefit =
Operational Savings – (Implementation Costs + M&V Costs + Audit Costs)

## Slide 6: 1.1. Objectives of energy audit levels
Objective of enterprise
Other benefit:
  Reduce emissions and other environmental impacts
  Increase the availability of non-renewable energy sources
  Reduce energy costs for customers, not only reducing consumption but also reducing the need for overall investment in the energy supply system
  Enhance competitiveness and increase productivity

## Slide 7: 1.1. Objectives of energy audit levels
Energy audit levels
Preliminary Energy Audit: Provides an overview without in-depth financial and technical details. It is the initial step before conducting an IGA.
Detailed Energy Audit: Focuses on identifying energy efficiency measures but lacks in-depth financial analysis as in IGA.
Investment Grade Audit (IGA): The highest level, offering a comprehensive, detailed analysis, including technical, financial, and risk assessment of proposed energy-saving measures.
As an extension of the detailed audit

## Slide 8: 1.2. Energy audit steps
Energy Audit Process – Overview
1. Audit Initiation
2. Off site data collection & Planning
3. On- site data collection
4. Energy balance
5. Analyze potential measures
6. Recommended measures
7. Report

## Slide 9: 1.2. Energy audit steps
Energy Audit Process – Implematation Steps
Step 1: Start the audit
› Define the scope
› Consult with stakeholders
› Determine the enterprise needs
Step 2: Collect enterprise data
› Utility Bills
› Review drawings and specifications
› Review specific issues
› Capital improvement plan

## Slide 10: 1.2. Energy audit steps
Energy Audit Process – Implematation Steps
Step 3: Conduct data collection at the enterprise
  Conduct interviews
  Equipment inventory
  Operational & maintenance assessment
  Condition assessment
Step 4: Determine the Energy Balance
  System Boundaries
  Energy/Demand by User
  Energy Input = Energy Consumed

## Slide 11: 1.2. Energy audit steps
Energy Audit Process – Implematation Steps
Step 5: Identify/Analyze Solutions
  Equipment Usage Model
  Equipment Condition Assessment/Technology Upgrade
  Operating Model/Process and Improvement
  Needs Assessment
  Calculate Savings Potential
Step 6: Selecting Solutions
  Energy Savings
  Cost Savings
  Return On Investment
  CO2 Emission Reductions
  Operating & Maintenance Cost Savings

## Slide 12: 1.2. Energy audit steps
Energy Audit Process – Implematation Steps
Step 7: Prepare the audit report
  Select a reporting plan for your enterprise
  Write a report outline
  Describe construction activities and equipment (can be changed within agreed scope)
  Analyze the energy balance
  Present repots
  Provide a summary of investment plans and potential savings
  Submit recommendations

## Slide 13
2.1. Background and expected results
2.2. Preliminary audit process
2.3. Preliminary assessment of EE potential
2.4. Reporting
2. Preliminary energy audit

## Slide 14: 2.1 . Context and outputs
Objective
  Identify if there is an opportunity – small but significant investment in a preliminary audit, identifying potential for the EPC project
  Identify scope for a more detailed audit
  Develop a target list to make the investment of time/money in a detailed audit more meaningful
  Build better relationships with stakeholders
  For ESCO: Analyze the proposed concepts for the enterprise owner

## Slide 15: 2.1 . Context and outputs
Effort and accuracy
  Time: 1-2 days at the enterprise, 3-5 days at the office
  Based mainly on available documents (drawings, electricity bills, maintenance note, etc.)
  Accuracy: ± 30% of savings and ± 30% of costs
  Use based on experience and/or benchmarks to analyze and calculate potential savings

## Slide 16: 2.1 . Context and outputs
Output by activity
- Start the audit
- Obtain preliminary information
(collect business data)
Activity
- View enterprise interests – of leader and employees
- Identify sales locations
- Review available preliminary information before visiting the enterprise
Output

## Slide 17: 2.1 . Context and outputs
Output by activity
Enterprise visit
Energy balance
Analysis and solution selection
Report
Presentation
Activity
Equipment survey, discussion with managers/executives
User analysis
Estimate potential and identify most suitable projects
Report results
Discuss results with customers
Output

## Slide 18: 2.2 . Preliminary audit process
Before the preliminary audit
The ESCO business development team needs:
  Conduct screening analysis
  Presentation of ESCO concept to client
  Check whether the client is credible (preliminary)
  Calculate the client’s benefits of implementing EE solutions
  Determine the client’s strategic position
  Determine the scope of the preliminary audit
The technical team responsible for performing the audit needs to have a good understanding of:
  Pricing structure
  Local standards
  Weather statistics
  Energy intensity statistics
  Available technologies and budgets

## Slide 19: 2.2 . Preliminary audit process
Before the preliminary audit
Collect and analyze information BEFORE visiting the facility (as much as possible):
    Basic information about enterprise
    Energy Bills
    Compare with Similar Establishments (Benchmarking)
Source : CIPEC Industrial Program

## Slide 20: 2.2 . Preliminary audit process
Before the preliminary audit
    Assess potential by comparing
    Help sell projects to clients

## Slide 21: 2.2 . Preliminary audit process
Before the preliminary audit
Collect basic information about enterprise
  Functions
  Architectural, mechanical and electrical drawings and specifications
  Control system drawings
  Operating hours/operational records
  Year of construction
  Energy bills for the last 3 years
  Each type of energy used
  Monthly production level (for the plant) for the last 3 years
  Future plans of the business
Collect basic information about enterprise
    Specific operational issues (contour, structure, obsolete equipment, etc.)
    Existing mechanical system testing and balancing reports
    Any existing energy efficiency studies
    Standards, codes and guidelines used to design the building as well as new standards and codes that must be met
    A brief meeting with the client is often the best way to check what information is available to them

## Slide 22: 2.2 . Preliminary audit process
Energy Bill Analysis – BEFORE Your Visit
  Analysis of energy bills of the last 3 years
    Electricity, Gas, Fuel Oil
      Focus on analyzing the last year
      Check consistency with the previous 2 years
  Summary of bills and average costs, peak costs and marginal costs
  Establish annual energy consumption standards in m2 kWh/m2 for buildings
  Check for power factor penalty
  Check if demand is sufficient
  Check for abnormal errors/patterns
    If there is no explanation, it may be due to a faulty electricity meter
    Should Investigate as compensation may be available from the electricity company
  Check if the applicable rate is the best, taking into account current energy usage patterns

## Slide 23: 2.2 . Preliminary audit process
Before the preliminary audit
Comparison between energy bill and FACTORY production level – BEFORE visiting
  Establish intensity index (energy per unit of production)
  - Not the best index but an initial analysis
  Construct a regression curve of output against energy to determine the baseline consumption of the enterprise
  - Will be presented in more detail when analyzing the baseline data
  Construct a curve to plot the output

## Slide 24: 2.2 . Preliminary audit process
Before the preliminary audit
Questionnaires can be sent in advance to collect preliminary information before visiting the enterprise.
Refer to the survey questionnaire below.

## Slide 25: 2.2 . Preliminary audit process
Before the preliminary audit

## Slide 26: 2.2 . Preliminary audit process
Before the preliminary audit- Survey form
Part 1 – General Information
Enterprise information: Address, telephone, email …
Activity
Number of employees, energy consumption data, energy systems
Available M&E charts, available logbooks, etc.
Part 2 – Monthly Energy Consumption Data
Monthly Consumption Data of
Electricity; Fuel; Water; Use Objective; Price
Section 3 – Production
Monthly Data: Raw Materials and Output
Section 4 – Energy Systems:
Energy consuming systems that may be available in the enterprise: Type, Quantity, Capacity, Operation of
Lighting, Compressors, Refrigerators & Air Conditioners, Boilers/ Furnaces, Engines
Part 5 – Energy Management:
Energy management systems in place, ISO?
Energy manager, contact details
Has the enterprise been audited
EE potential/expected cost savings, are there any campaigns in progress?

## Slide 27: 2.2 . Preliminary audit process
Before the preliminary audit - Field visit to the enterprise
  1-2 ESCO representatives visit the project/factory
  Identify the main plant systems, their capacity, operating time and current condition
  - Identify equipment that has been recently replaced (this can reduce the potential, especially high potential equipment such as chillers, boilers, air compressors, etc.)
  Identify the technology used in each equipment
  Identify the control system used (timers, individual pneumatic panels, direct digital controls, BMS…)
  Verify the preliminary information received

## Slide 28: 2.2 . Preliminary audit process
Before the preliminary audit - Field visit to the enterprise
Old chiller at the end of its life
New chiller

## Slide 29: 2.2 . Preliminary audit process
Before the preliminary audit - Field visit to the enterprise
Interview technical/operational managers – during enterprise visit
  System operating hours
  Operating procedures and set points
  Systems, processes and their characteristics, etc.
  Current control systems and schedules
  Should have printed copy if possible
  Identify issues related to on-site equipment operation and maintenance
  Chiller: is the heat exchanger clean?
  Boiler: is it regularly tuned for efficiency, are tubes cleaned, is water treated?

## Slide 30: 2.2 . Preliminary audit process
Before the preliminary audit - Field visit to the enterprise
Interview technical/operational managers – during enterprise visit
  Verify information from drawings and specifications
  Identify peak hours
  Identify equipment that uses electricity during peak hours
  * ASK QUESTIONS when visiting a enterprise *

## Slide 31: 2.2 . Preliminary audit process
Before the preliminary audit - Field visit to the enterprise
Industrial processes – when visiting an enterprise
  Raw material description and quantification
  Energy input and water consumption at each production process
  Temperature, pressure and flow rate
  Conversion process to final product
  Control mode
  Lighting requirements
  Operating schedule and potential for reduction during peak hours
  Analysis - evaluation criteria
  Owner's Desire for the Project
  Achieve Financial Payback Threshold
  Return < x years
  IRR > x %
  Low/No Cost: Low Investment Cost and High Savings
  Low Risk Solution: Ensure Savings

## Slide 32: 2.3. Preliminary assessment of EE potential
Energy efficiency solutions – Based on experience
Experience in determining potential is presented in the section below:
  Experimental auditors can quickly identify a list of potential EE solutions;
  The technologies will be detailed in the following sections;
  Illumination
  Incandescent: CFLs use 4 – 5 times less energy
  T10 fluorescent lamps: 40W or 36W lamps can be replaced by T8, T5 (Tri phosphor) lamps with electronic ballasts or LEDs
  Magnetic ballasts: can be replaced by electronic ballasts
  Mercury vapor lamps: can be replaced by HPS lamps
  Incandescent exit lamps: can be replaced by CFLs or LEDs

## Slide 33: 2.3. Preliminary assessment of EE potential
Energy efficiency solutions – Based on experience
Chart: Lumens per watt
| Incandescent | Halogen A-line | White LED | Mercury Vapour | Linear Fluorescent | Compact Fluorescent | High-Pressure Sodium | Metal Halide | Induction
 | 10 | 12 | 70 | 25 | 30 | 40 | 50 | 70 | 60
 | 7 | 10 | 55 | 35 | 80 | 30 | 90 | 45 | 44
25-60
30-110
40-70
Lamp performance

## Slide 34: 2.3. Preliminary assessment of EE potential
Energy efficiency solutions – Based on experience
Illumination
  Calculate the electrical power per unit area – good efficiency index
    Benchmark against reference values ​​W/m2
    For example, classroom:
      Current: 19 W/m2
      upgraded efficiency: 8.6 W/m2
  Use a luxmeter to check the current brightness in different areas.
    Identify overexposed or underexposed areas

## Slide 35: 2.3. Preliminary assessment of EE potential
Energy efficiency solutions – Based on experience
Illumination
Look at the control system
  Can it be turned off in all unoccupied areas?
  Are several zones on the same circuit?
Look at the spotlight assembly of the lighting system
  Color-changing/broken spotlights retain most of the light
  Can clear spotlights be replaced?
Look at the light fixture itself
  If the reflective surfaces are slightly yellow, new reflectors can be used to increase the lumen output from the luminaire.
  Opportunity to reduce the number of tubes while maintaining the same brightness
Motion detector and presence sensor

## Slide 36: 2.3. Preliminary assessment of EE potential
Energy efficiency solutions – Based on experience
  Motor
Is there an energy efficient motor?
If not = potential reduction is 2 – 10% depending on size
The larger the motor, the lower the potential reduction

## Slide 37: 2.3. Preliminary assessment of EE potential
Energy efficiency solutions – Based on experience
  Motor
Are the ventilation and pumping systems equipped with frequency converters?
If the heating and cooling load control is changed by butterfly valves or regulating valves, installing a frequency converter can help save significantly
If the system inflow is reduced by 20%, the power consumption can be reduced by about 50%.
  Motor
VSD inverter warning
Difficult to perform on systems: High-rise project (e.g. open-circuit cooling towers on high-rise buildings)
Difficult to perform on refrigeration systems (water column pressure and lubrication issues)
BE CAREFUL with chiller main circuits (can freeze the evaporator)

## Slide 38: 2.3. Preliminary assessment of EE potential
Energy efficiency solutions – Based on experience
  Ventilation
Is there a constant flow system under all heating and cooling conditions?
Can be changed to variable current
Is the mixture temperature control system fixed?
Can it be adjusted using a zone signal or based on outside air temperature?
Source: www.flaktwoods.com
  Ventilation
  Is outside ventilation as required or too high?
  Check occupancy and local standards for outside ventilation

## Slide 39: 2.3. Preliminary assessment of EE potential
Energy efficiency solutions – Based on experience
  Ventilation
Is the throttle valve closed tightly?
  Especially for systems that operate during idle hours, close the outside air damper tightly
  Usually for heating or cooling purposes
Source: http://arrowunited.com

## Slide 40: 2.3. Preliminary assessment of EE potential
Energy efficiency solutions – Based on experience
  Ventilation
Is there evidence of a poor connection to the fan inlet?
  The bend at the fan inlet affects the system and causes low efficiency.
AMCA Publication 2011
Discuss the effect of input and output connections on fan performance

## Slide 41: 2.3. Preliminary assessment of EE potential
Energy efficiency solutions – Based on experience
  Ventilation
Is there a large exhaust pipe so that hot or cool air can be recovered?
  Freon tube exchanger, plate exchanger or heat wheel can be installed around the coil.
Source: www.zigersnead.com

## Slide 42: 2.3. Preliminary assessment of EE potential
Energy efficiency solutions – Based on experience
  Cooling system
Are there any idle temperature settings?
How old are the chillers and how efficient are they?
  The energy consumption of new chillers can be 40 – 50% less than chillers that have been used for 20 years.

## Slide 43: 2.3. Preliminary assessment of EE potential
Energy efficiency solutions – Based on experience
  Freezing system
Is the condensate temperature control device fixed?
  Temperature-based adjustment opportunities
Is the coolant temperature constant?
  Adjustable based on cooling load
Condensate tower

## Slide 44: 2.3. Preliminary assessment of EE potential
Energy efficiency solutions – Based on experience
  Cooling system
Is it expensive to operate during peak hours?
  Consider an ice storage system
Source: inhabitat.com

## Slide 45: 2.3. Preliminary assessment of EE potential
Energy efficiency solutions – Based on experience
  Heating System
Is there a night time reset or thermostat?
Is there a steam system or hot water heating?

## Slide 46: 2.3. Preliminary assessment of EE potential
Energy efficiency solutions – Based on experience
  Boiler
Is the flue temperature high?
  If the temperature is above 600C compared to the average temperature (steam or water), it may be a sign of low boiler efficiency.
What types of control systems are used? Simply on-off, linkage control?
  Adjust by mechanical linkage so that fuel usage and air flow can be improved
Source: www.econologie.com
Is there a bottom discharge recall?

## Slide 47: 2.3. Preliminary assessment of EE potential
Energy efficiency solutions – Based on experience
  Boiler
Is there a cogeneration requirement for heat and power?
  Cogeneration equipment research
Source: www.necanet.org

## Slide 48: 2.3. Preliminary assessment of EE potential
Energy efficiency solutions – Based on experience
Air Compressor
Do you hear air leaks?
  If you hear it, you need to upgrade.
Air into the machine room or outside?
  If the air outside is colder, it will work more efficiently.
How many years has the air compressor been used?

## Slide 49: 2.3. Preliminary assessment of EE potential
Energy efficiency solutions – Based on experience
Hot Water
Is there a high demand for hot water?
  A latent heat recovery system can be installed for the hot water boiler with an efficiency of 98%
  Heat recovery from the condenser of the refrigeration compressor

## Slide 50: 2.3. Preliminary assessment of EE potential
Energy efficiency Solutions – Preliminary Assessment
  At the preliminary audit stage, the assessment is at ± 30%
    Preliminary analysis tools can be used, such as the Retscreen tool
    Benchmark against previous projects or best practices
    Return to contour calculation
  Determine potential savings – not the only number
  Always write down your assumptions and the basis for your preliminary calculations
  Investment reporting could begin in a few months
    Record your ideas.
    Identify hypotheses that would require improvement in the investment report.

## Slide 51: 2.3. Preliminary assessment of EE potential
Energy efficiency Solutions – Preliminary Assessment
Annual energy efficiency (internal)
  Actual system consumption for which the target has been set
  Total direct savings
  Are there any cross-effects that need to be considered?
  Consider the guarantee factors and adjust if detailed data is lacking
  DO NOT sell too many projects to clients if you are not confident that you can achieve the expected results
  In competitive bidding, a strong stance is the best way to avoid encountering companies with poor capabilities.

## Slide 52: 2.3. Preliminary assessment of EE potential
Energy efficiency Solutions – Preliminary Assessment
Monetary value of energy efficiency (internal)
  The value of the savings is based on the pricing structure
  Includes detailed calculations of the savings
Cost of modification
  Preliminary stage: only provides budget estimates
  Usually based on:
    Savings x payback period (benchmark against other projects)
    Based on experience (cost per kWh installed for boilers, chillers, per m2 for lighting, etc.)

## Slide 53: 2.3. Preliminary assessment of EE potential
Energy efficiency Solutions – Preliminary Assessment
M&V Agreement (internal)
  Start thinking: how can we measure savings to ensure savings are achieved?
  Are most of the savings measurement options appropriate?
  Each solution may be different if the approach for each solution is adopted
  Is a holistic approach to building a business feasible for this type of business?
  Outline which measurement methods can be applied
    Measure the same parameters before + after project implementation
    Compare invoices before + after
    During the measurement period

## Slide 54: 2.3. Preliminary assessment of EE potential
Energy efficiency Solutions – Preliminary Assessment
Risk analysis (internal)
  Must be performed for each proposal
  Allows the ESCO with the proposal to qualify to manage hypothetical changes as they occur.
  Some ESCOs provide risk analysis by changing
    implementation costs
    Actual and projected savings scenarios
    Retscreen is a great tool for performing Monte Carlo analysis.
  ESCO can decide on the next step of the project
  More risk = higher cost to compensate for the risk

## Slide 55: 2.3. Preliminary assessment of EE potential
Energy efficiency Solutions – Preliminary Assessment
Select EE solutions based on:
  Financial profit
  Easy to implementation
  Risk analysis
  Customer readiness…

## Slide 56: 2.4. Report
Preliminary audit report
  Objective
  Summarize the results of the preliminary audit
  Convince the enterprise owner to invest
  Make it easy and comprehensive for busy managers to read
  Submit a professional, concise and concise report

## Slide 57: 2.4. Report
Preliminary audit report
  Report structure
  Summary
  Characteristics and current status of enterprise operations
  Brief description of electrical and mechanical systems
  Summary of current energy consumption
  Proposals and recommendations for EE solutions
  Conclusion

## Slide 58: 2.4. Report
Preliminary audit report
The report structure is specified in Circular 09/TT-BCT
CHAPTER 1. SUMMARY
1.1. Energy efficiency potential
1.2. Ability to implement energy efficiency solutions
1.3. Proposed implementation plan
CHAPTER 2. INTRODUCTION
2.1. Introduction of the audited unit and auditor
2.2. Scope of energy audit
2.3. Measurement methods and equipment
CHAPTER 3. ENTERPRISE ACTIVITIES
3.1. Development history and current status
3.2. Operation and production methods

## Slide 59: 2.4. Report
Preliminary audit report
The report structure is specified in Circular 09/TT-BCT
CHAPTER 4. PRODUCTION LINE DESCRIPTION
4.1. Production lines
4.2. Energy efficiency potential
CHAPTER 5. ENERGY DEMAND AND SUPPLY CAPACITY
5.1. Energy supply and consumption
5.2. Fuel supply and water consumption
CHAPTER 6. FINANCE AND TECHNICAL CONSTRAINTS
6.1. Technical, technological and environmental issues
6.2. Economic solutions and assessment
CHAPTER 7. ENERGY EFFICIENCY POTENTIAL

## Slide 60: Discuss

## Slide 61
Thank you!