## Slide 1
Module 17: Measurement and verification

## Slide 2: CONTENT
1. Introduce
2. Main concept
3. M&V planning
4. Key issues
5. Statistic

## Slide 3: Concept of M&V
What is the concept of M&V?
M = Measurement
V = Verification
“Measurement & Verification (M&V) is the process of using measurements to determine the actual savings achieved in a business through an energy management program.”
Source: IPMVP Core Concepts 2014, Chapter 3, 3.5
IPMVP: International Performance Measurement and Verification Protocol
Developed by the organization EVO (Efficiency Valuation Organization)
It provides 4 M&V methods: Option A, B, C, D.
Objective: To verify energy savings results transparently and accurately

## Slide 4: Concept of M&V
What is the concept of M&V?
“Measurement & Verification (M&V) is the process of planning, measuring, collecting data, analyzing, measuring, verifying, and reporting energy performance or improvements in energy efficiency within a defined M&V boundary.”
Source: TCVN ISO 2015:2016, equivalent to ISO 50015:2014
ISO 50015 is an international standard within the ISO 50000 series on energy management.
It provides guidelines for implementing M&V in the context of energy management systems.
It focuses on the entire process from establishing a baseline, collecting data, and reporting results.
Two different sources provide procedures, processes, and methods for measuring and verifying energy performance with similar and different goals to serve different purposes for measuring and verifying the effectiveness of Energy Saving solutions.

## Slide 5: The Purpose of M&V
Increase energy savings potential
Store data on financial transactions
Enhance financing for energy-saving projects in a fundamental way
Improve design, operation, and maintenance
Explain the reasons for changes in a company’s budget
Support the evaluation of the program’s effectiveness
Provide training for company staff on the impacts of energy
Improve the score in Green Building Certification or sustainability rating systems such as LEED (Leadership in Energy and Environmental Design).

## Slide 6: IPMVP and ISO 50015
Define the Energy Baseline (EnB).
Focus on accurate, transparent, and repeatable data.
Used to measure and report energy savings performance.
Requires comprehensive data collection and processing to avoid result discrepancies.

## Slide 7: IPMVP and ISO 50015
IPMVP
Suitable for ESCO projects, focusing on the energy savings of specific solutions.
There are 4 specific methods for M&V (Option A, B, C, D).
Option A: Measure key parameters of the equipment or solution.
Option B: Measure all parameters of the equipment or solution.
Option C: Measure the entire plant.
Option D: Simulate the entire plant.
Focus on measurements after the project implementation.
Detailed and specific for each equipment and project.
ISO 50015
Serves comprehensive energy management, in compliance with ISO 50001.
Does not specify a particular method but focuses on standard processes.
Focuses on both the management process and energy improvement.
More general, suitable for various types of organizations.
IPMVP is the appropriate method for the goals of ESCO projects and is therefore the focus of this module.

## Slide 8: Concept of M ...&….V
M: Measurement
“Đo lường is Measurement
Not monitoring
(Monitoring is a separate activity to determine savings. It is the process of observing energy usage for the purposes of forecasting, cost control and diagnosis.)
V: Verification
“Xác nhận is Verification
Verify operation
Verify independence:
Why, Who, What, When?
Verify renovation of insulation system

## Slide 9: Concept of M ...&….V
Measure savings:
Saving is not using energy so we cannot measure what we do not have.
We cannot ‘measure’ savings!
We measure energy use.
We analyze measured energy usage to determine savings.
Confirm savings Measurement and calculations are used to Confirm that the energy saving idea has worked. There were three issues that were discussed: - Confirm the operation; - The role of independent 'certification officers’; - Continuously validate the effectiveness of unmeasured parts by isolating the created system.

## Slide 10: Energy Saving Level
IPMVP Base Savings:
Savings = energy of the base stage - energy of the reporting period +/- Adjustment
Baseline + Adjustment
Saving
Measured Energy
Base Period
Reporting Period

## Slide 11: Adjust
Chart: 
| Trước dự án | Sau dự án năm 1 | Sau dự án năm 2
Tiêu thụ năng lượng | 5 | 3 | 5
Tiêu thụ năng lượng bổ sung | 1
Tiết kiệm năng lượng nhờ dự án | 0 | 1.5 | 1.8
Năng lượng giảm do sản xuất ít hơn | 0 | 0.5 | 0
Can be adjusted little, simply or complexly. Adjustments can include technical calculations. The degree of adjustment depends on: - The need for accuracy, - The complexity of the factors that drive energy use, - The number of devices whose effectiveness is assessed (e.g. 'measurement range'), - Budget available.
Before the project
After 1 year
Reduced energy due to less production
Saving energy due to the project
Additional energy consumption

## Slide 12: “Savings” or “Avoidance”?
Energy users often want to know how much they would have to pay for their energy bills if they did not take energy-saving actions. They want to know how much energy costs they have avoided.
To report avoided costs, M&V engineers adjust baseline energy usage to match the reporting period. They sometimes simply refer to this as “savings” to mean avoided costs, as using this term risks confusion with accounting terminology.
Accountants typically use the word “savings” to mean “cost reduction.” They do not perform adjustments.
Therefore, when discussing “savings,” we must be very careful to explain what we mean.
We must report the set of conditions we are using to define “savings.”

## Slide 13: M&V Options
The measurement range is the whole plant
Engine+ VSDs
Scope of the system to be renovated
Whole Facility Methods (Options C and D): Measure all effects resulting from facility upgrades:
Includes upgrades and other changes (intentional and unintentional).
Commonly uses metering at the energy source.
Adjustments can be complex.
Retrofit Isolation Methods (Options A and B): Measure only the impact of the upgrades.
Savings are unaffected by changes outside the measurement boundary.
Typically requires specialized metering equipment for the isolated system.
Adjustments can be simpler.
Notes: 40
12
10
9
9
9
9
9
9
9
Dwell on the wide vs narrow boundary issue

## Slide 14: M&V Options
Criteria | Option A | Option B | Option C | Option D
Measure | Partial + Estimate | Full Measurement | Facility-wide measurement | System-wide simulation
Accuracy | Average | High | High | High
Measurement Cost | Low | Average | High | Very High
Complexity | Simple | Average | High | Very High

## Slide 15: M&V Options
Option A: Measure Key Parameters and Estimate Remaining Variables
This method combines partial measurement with the estimation of unmeasured variables.
Advantages:
Low cost, Easy to implement, Suitable for simple equipment such as LED lights or small motors
Disadvantages:
Low accuracy due to the inclusion of estimated factors
Not suitable for complex systems
Relies on assumptions and technical documentation
Recommendations:
Use when controlling measurement costs is a priority.
Avoid using for complex systems requiring high accuracy.

## Slide 16: M&V Options
Option B: Fully Measure the Necessary Parameters of the Retrofitted Equipment/System
Fully measures all variables to accurately assess energy savings performance.
Advantages:
High accuracy: Actual measurements, not reliant on estimations.
Suitable for complex systems: Such as HVAC, pumping systems, and production lines.
Optimal for ESCO projects: Ensures transparency in energy performance contracts.
Disadvantages:
High measurement costs: Requires extensive metering equipment.
Complex procedures: Demands a highly skilled technical team.
Limited applicability for small systems: Inefficient for simple or low-consumption equipment.
Recommendations:
The optimal choice for large projects requiring high measurement accuracy.
Ensures transparency, making it suitable for ESCO projects.
Use when comprehensive measurement is needed to eliminate estimation factors.
Combine with other standards, such as ISO 50015, to enhance reliability.

## Slide 17: M&V Options
Option C: Whole-Facility Measurement Method
This method focuses on analyzing aggregate data for the entire energy-consuming system.
Uses overall data such as electricity bills, output production, or readings from main utility meters.
Focuses on changes in total energy consumption for the entire system.
Applied when individual equipment measurement is not feasible.
How to Implement Option C
Collect overall energy data: Electricity bills or main meter readings.
Establish a baseline: Analyze energy consumption data before implementing improvements.
Measure and compare: Compare energy consumption levels before and after deploying solutions.
Adjust for variations: Account for factors like weather, production output, or occupancy changes.

## Slide 18: M&V Options
Option C:
Advantages
Wide scope: Evaluates the entire facility, not limited to specific equipment.
Low cost: No need for extensive metering installations.
Ease of implementation: Requires only aggregate data from utility meters or bills.
Suitable for large facilities: Office buildings, hotels, and industrial plants.
Disadvantages
Moderate accuracy: Cannot precisely attribute savings to individual equipment.
Susceptible to external fluctuations: Influenced by changes in weather, production capacity, or staffing levels.
Not suitable for small projects or individual equipment

## Slide 19: M&V Options
When to Use Option C
Assessing energy efficiency for an entire facility or building.
When aggregate energy consumption data is available (e.g., bills, main meters).
When detailed measurement of individual equipment is not required.
Examples:
Evaluating EE improvements after upgrading an entire HVAC system in a building.
EE projects for a large manufacturing facility.
Conclusion
Option C is an ideal choice for comprehensive energy performance evaluations.
Suitable for large facilities where aggregate energy data is available.
Applied when a holistic evaluation is needed without detailed measurements of individual equipment.
Can be combined with other options (A, B) to enhance accuracy for deeper analysis.

## Slide 20: M&V Options
Option D: Simulation-Based Method
This method uses energy simulation with specialized software to evaluate energy consumption and estimate savings.
Applied when direct measurement is not feasible or for large-scale retrofits.
Commonly used in new construction or major renovation projects.
How to Implement Option D
Gather input data: Equipment specifications, technical drawings, and building characteristics.
Develop a simulation model: Use specialized software such as EnergyPlus, eQUEST, or DesignBuilder.
Establish a baseline: Simulate energy consumption before implementing improvements.
Verify results: Compare simulated data with actual data (if available).

## Slide 21: M&V Options
Option D: Simulation-Based Method
Advantages
High accuracy: Provides detailed analysis of multiple variables.
Suitable for large projects: Especially for new buildings or major retrofits.
Applicable when actual data is unavailable: Simulated data can serve as a baseline.
Disadvantages
High cost: Requires specialized software and a highly skilled technical team.
Complex: Time-intensive to build and validate the model.
Reliant on model accuracy: Errors may occur if the model does not accurately reflect real-world conditions.
When to Use Option D
When direct measurement is not possible.
To evaluate energy performance for new construction.
For major renovation projects requiring detailed analysis.

## Slide 22: M&V Options
Conclusion
Option D is a suitable method for new construction or major retrofits requiring comprehensive simulations.
Ensures high accuracy but demands significant cost and technical expertise.
Ideal when comprehensive modeling is needed and actual data is unavailable.
Can be combined with Options A, B, and C in large-scale projects to enhance accuracy.

## Slide 23: M&V Costs
One of the critical factors in implementing M&V is the cost. This is a significant concern because, in many cases, M&V costs can be substantial and do not directly contribute to energy savings. However, they serve as an essential basis for ESCOs to receive payment from the facility.
Key Factors Influencing M&V Costs:
Quality of meters: The precision and reliability of measurement equipment.
Number of independent variables to be monitored: More variables increase complexity and cost.
Measurement and reporting frequency: Higher frequency requires more resources and increases costs.
Duration of the baseline and reporting periods: Longer periods require extended monitoring efforts.
Sample size: If not all equipment is measured, the sample size affects the cost and accuracy.
Shared use of meter information: Costs can be reduced by sharing meter data for multiple purposes.
Skill level required: Skilled personnel are often necessary, which can increase costs.

## Slide 24: M&V Costs
Limit M&V cost
Saving
M&V cost
So how much is enough?
Complexity of the process
Monthly check
Check 1 simple time

## Slide 25: M&V Costs
How Much Should M&V Cost?
Typically, the total annual cost for determining savings should be less than 10% of the annual savings. However, it may exceed this maximum in special circumstances.
3-5% is a more common range for ESCO projects.
0% is often chosen (considered as “deemed savings”). No measurement means uncertain savings. This is NOT an IPMVP method
Recommendation:
There should be a balance between cost and accuracy, tailored to each project’s specific needs.

## Slide 26: Statistic
What is statistic?
Statistics = Data Analysis Tools
Why do we use statistics?
  To better understand measurement data.
  To describe them in a consistent and unified way.
  To decide on goals
Statistics is concerned with the collection, analysis, interpretation, and presentation of numerical data.

## Slide 27: Statistic
Sampling procedure
Determine the overall.
Determine if the overall is homogeneous or heterogeneous. If heterogeneous:
Separate the overall in groups.
Choose a simple or stratified method.
Decide on acceptable precision and reliability.
Estimate or assume the cv value; calculate the sample size.
Perform the sampling.
Calculate and report the actual cv value and the precision of the cv value.

## Slide 28: Statistic
Regression analysis
The statistical method used is to find the relationship between a set of variables:
Dependent variables:
- Energy
Independent variables:
- Weather
- Usage
- Production volume
- Time
- ...

## Slide 29: Statistic
Regression steps
Step 1: Collect data
    Collect Important Data
    Check for Correlations
    Input Data
Step 2: Review data
    Check the summary table
Step 3: Check the energy curve and cycle
Step 4: Scatter Points
  Graphical representation of data
Step 5: Correlation
  Measure of the strength and direction of the relationship between variables
Step 6: Regression
  A model predicts one variable from other variables.

## Slide 30: Statistic
Scatter Points
Visual display:
  Strength of the Relationship Between Variables
  Direction of the relationship between variables
  Linear and nonlinear relationships
  Existence of outliers
Chart: 
| 29 | 36 | 34 | 31 | 31 | 28 | 36 | 30 | 35 | 36 | 35 | 28 | 30 | 32 | 33 | 34 | 35 | 36 | 28 | 30 | 32 | 33 | 34 | 35 | 36 | 28 | 30 | 32 | 33 | 34 | 35 | 36 | 28 | 30 | 32 | 33 | 34 | 35 | 36
Mjerni rezultat | 7.1 | 6.1 | 5.9 | 6.5 | 6.5 | 7.5 | 6.2 | 6.8 | 5.6 | 6.2 | 6.5 | 6.7 | 6.8 | 6.6 | 5.7 | 5.9 | 6.3 | 6.1 | 7.4 | 6.3 | 5.9 | 6.1 | 5.7 | 6.1 | 6.2 | 6.1 | 5.6 | 6.2 | 5.4 | 5.3 | 4.9 | 5.3 | 6.8 | 6.8 | 6.4 | 6.4 | 5.3 | 5.7 | 6.1

## Slide 31: Statistic
Why Does It Matter?
Savings are calculated as:
Savings = (Baseline energy - Reporting period energy)
+/- Routine adjustments
+/- Non-routine adjustments
Baseline energy + routine adjustments can be derived from baseline data using different modeling approaches.
Baseline energy data can be sampled to minimize costs.
Savings are calculated from measured data, which, by nature, may not be entirely accurate and inherently carry some level of uncertainty.

## Slide 32: Statistics
Modeling
We may not have a specific basis to determine exact energy consumption.
However, we can observe the relationship between energy use and changes in production rates, which can lead to an empirical model that assumes how energy consumption varies with production levels.
Considering seasonal variations throughout the year also provides a quantitative understanding of energy consumption.
Establishing a baseline using statistical methods is extremely useful.
All models are wrong, some models are useful
Chart: 
| 86 | 13.5 | 4.5999999999999996 | 0.30000000000000032 | 0 | 0 | 0 | 0 | 3.2 | 6.6 | 23.7 | 76.599999999999994
Predicted | 109022.2015 | 92074.1033 | 89993.5781 | 88988.3805 | 88918.2505 | 88918.2505 | 88918.2505 | 88918.2505 | 89666.3045 | 90461.1118 | 94458.5254 | 106824.7929
CI- | 103095.5888 | 86147.4906 | 84066.9654 | 83061.7679 | 82991.6378 | 82991.6378 | 82991.6378 | 82991.6378 | 83739.6918 | 84534.4992 | 88531.9127 | 100898.1802
CI+ | 114948.8142 | 98000.7159 | 95920.1908 | 94914.9932 | 94844.8632 | 94844.8632 | 94844.8632 | 94844.8632 | 95592.9172 | 96387.7245 | 100385.138 | 112751.4056
 | 106713 | 90605 | 94490 | 90177 | 91876 | 85745 | 86358 | 92293 | 86430 | 91369 | 90388 | 110718
This type of question has been answered through regression analysis of statistical techniques. We will later cover useful aspects of statistical techniques in the chapter on statistics and how this descriptive tool and method can help.

## Slide 33: Statistics
Construction of energy use facilities:
Let's look at measuring the power of 1288 identical fluorescent light bulbs in a building.
Can we measure each type of lamp separately?
Is there a way to limit the number of measurements by sampling a small sample without increasing the uncertainty in our assessment if it goes beyond some acceptable limit?
Taking sample
This question is answered through sampling analysis of statistical techniques.
Chart: 
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22
 | 100 | 120 | 134 | 102 | 110 | 90 | 78 | 104 | 110 | 102 | 101 | 103 | 103 | 98 | 107 | 110 | 89 | 103 | 108 | 95 | 100 | 87
Chart: 
| 62.454545454545283 | 72.454545454545467 | 82.454545454545467 | 92.454545454545467 | 102.45454545454552 | 112.45454545454552 | 122.45454545454552 | 132.45454545454538 | 142.45454545454538
Sample | 0 | 1 | 3 | 4 | 12 | 1 | 0 | 1 | 0
Distribution of Point Estimate | 0.018526 | 0.25781 | 1.6908 | 5.226 | 7.6125 | 5.226 | 1.6908 | 0.25781 | 0.018526
Distribution of Mean | 0.0090958 | 35.7058 | 0.0090958

## Slide 34: Statistics
There is no "correct" value measuring device. Any device used for measurement may have some measurement uncertainty.
Resolution, accuracy and precision (plus measurement error) are the most common influencing factors.
Uncertainty in measurement

## Slide 35: Statistics
In general, measurement uncertainty consists of many components.
We always consider:
Uncertainty of model
Uncertainty when taking sample
Uncertainty when measure
Because these contribute greatly to the uncertainty in determining the overall savings level.
Uncertainty in determining the level of savings
  Savings = (baseline energy - reporting period energy)
  +/- common adjustments
  +/- unusual adjustments
Chart: 
| 512 | 419 | 357 | 248 | 92 | 54 | 87 | 214 | 236 | 432 | 476 | 445 | 367 | 219 | 189 | 65 | 119 | 223 | 316 | 500
 | 137830 | 101620 | 82446 | 66371 | 18757 | 0 | 16087 | 63205 | 70131 | 100271 | 107476 | 136181 | 78767 | 48059 | 42488 | 5770 | 11447 | 40457 | 100890 | 135079
limite supérieure | 152635.2782 | 126992.6674 | 109897.5935 | 79843.3507 | 36829.9389 | 26352.313 | 35451.3039 | 70468.6327 | 76534.6267 | 130577.1183 | 142709.1063 | 134161.5693
limite inférieure | 110601.7528 | 84959.142 | 67864.0681 | 37809.8253 | -5203.5864 | -15681.2124 | -6582.2214 | 28435.1073 | 34501.1013 | 88543.593 | 100675.5809 | 92128.0439
outlierinf | 108034.4842 | 82391.8733 | 65296.7994 | 35242.5566 | -7770.8551 | -18248.481 | -9149.4901 | 25867.8387 | 31933.8327 | 85976.3243 | 98108.3122 | 89560.7753
outliersup | 155202.5469 | 129559.936 | 112464.8621 | 82410.6193 | 39397.2076 | 28919.5816 | 38018.5726 | 73035.9014 | 79101.8953 | 133144.387 | 145276.3749 | 136728.838
Chart: 
| 62.454545454545247 | 72.454545454545467 | 82.454545454545467 | 92.454545454545467 | 102.45454545454552 | 112.45454545454552 | 122.45454545454552 | 132.45454545454538 | 142.45454545454538
Sample | 0 | 1 | 3 | 4 | 12 | 1 | 0 | 1 | 0
Distribution of Point Estimate | 0.018526 | 0.25781 | 1.6908 | 5.226 | 7.6125 | 5.226 | 1.6908 | 0.25781 | 0.018526
Distribution of Mean | 0.0090958 | 35.7058 | 0.0090958

## Slide 36
Why and when to perform M&V planning?
Basic principles
Set measurement range
Base data
Measuring equipment
M&V planning

## Slide 37: Why should we make M&V plan?
The preparation of an M&V Plan is a recommended part of savings determination. It also allows to:
Direct actions.
Ensure proper information is archived for later use.
Resolve major issues in cold blood, before “money is on the table.”
The M&V Plan should be developed while energy conservation measures (ECMs) are being designed in order to:
include the cost of M&V when deciding project economics, and
record baseline data and methodology for savings calculations while baseline conditions are still measurable, while memories are fresh and before any savings happen.
You complete the design of any new metering equipment while the ECM design is being completed.

## Slide 38: M&V principles
In alphabetical order (English):
Accurate – as limited by budget
Complete – consider all effects, measure significant effects
Conservative – errors on low sides
Consistent – amongst reports and energy types
Relevant – focus on measuring selected key performance parameters
Transparency – full disclosure as defined in IPMVP Vol. I 2012, Chapters 5 and 6
See IPMVP Core Concepts 2014, Chapters 7 and 8

## Slide 39: Measurement range
Are we assessing the current energy usage of:
The whole factory?
A system or group of systems (lighting, HVAC, compressed air, steel mill heaters...)?
A part or group of parts (boiler, chiller, motor, lighting set, pump and fan...)?
To set the scope, you need to consider:
The parties' responsibilities for energy use and equipment renovation may vary;
Ability to track plant changes and changes in plant usage – within selected ranges;
The importance of influences beyond the chosen scope are called ‘Interactive Effects’.

## Slide 40: Baseline data
What is baseline data?
Baseline data that must be included in the base phase:
All energy use (and demand) data;
All independent variable data (for daily adjustments);
All other factors that have a significant effect on energy upon changes in base conditions (need occasional adjustment). These factors are called static coefficients, to distinguish them from variables that change from day to day.

## Slide 41: Baseline data
Independent variables
Independent variables are energy drivers that change frequently and have a significant impact on energy.
What frequent changes affect your plant's energy use?
How important is each influence?
How much does it cost to obtain data on each influence?
Choose wisely!

## Slide 42: Baseline data
Select independent variables
Choose as many parameters as possible to explain changes in the baseline.
Recommendation: choose only those parameters that are needed to reasonably explain changes in the baseline data.
  Q. What is reasonable?
  A. Statistics and uncertainty in IPMVP 1:2014 presents statistical terminology to help define “reasonableness” and techniques for selecting independent variables.

## Slide 43: Baseline data
Definition of static elements
Plant characteristics that influence energy use within the selected measurement range, but are not used as a basis for any permanent adjustment. These characteristics include constant characteristics, environmental characteristics, operation and maintenance. They may be constant or variable.

## Slide 44: Baseline data
Where do we get the data?
Energy data are obtained from electricity meters or energy bills, or insulation meters
Independent variable data are obtained from government weather stations, factory records, control systems, etc.
Static coefficients are obtained from factory records, control systems, etc.
For each data source, four factors should be considered:
    Data accuracy data
    Availability when we need
    Data reliability
    Cost of data collection

## Slide 45: Baseline data
Example
You are planning M&V for a recreation center. The improvements to be installed are high efficiency condensing boilers, efficient controls, etc. The old boilers are standard boilers. The boilers provide heat for the recreation center and for the swimming pool. It is estimated that 65% of the heat is used for the swimming pool, 35% is for space heating.
What are the independent variables and static coefficients here?

## Slide 46: Baseline data
Separating the layers - onion shape graph
A method to consider all independent variables and potential static coefficients throughout plant operations
Good internal management
Operation & Maintenance
Control
Device
Procedure
Service

## Slide 47: Measuring equipment
Size the meter for the measurement range.
Select the meter most of the time.
If accuracy beyond the available measurement range is important, use a two-stage flow meter: high flow and low flow
Prevent loss of accuracy if the data line is ‘cut off’ or software changes (8-bit data vs. 16-bit data)
Use the same meter for ‘before’ and ‘after’ data recording.

## Slide 48: Measuring equipment
Meters
Application | Tools
Electricity | True RMS Wattmeter, Power Meter
Illumination | Lux Meter, Hour Meter
Hours of use | Utilization Sensor (Data Logger)
Rotation speed | Revolution Meter (Contact, Strobe, and Visual)
Air flow | Anemometer
Pressure | Digital Manometer
Temperature | Digital Thermometer or Digital Data Logger
Humidity | Digital Humidity Meter
Air quality | Gas Analyzer: CO2
Combustion | Combustion Analyzer
Process | Data Logger – Process Signal
Liquid flow | Flow Meter – Continue in the next part

## Slide 49: Measuring equipment
Meter data management
Record all adjusted data on raw data;
Record all meter system maintenance activities;
Convert data into useful information by doing the following two ways:
  Time function to check the value of the data;
  The device function can change, for example fuel used compared to production or outdoor temperature;
Building stored procedures

## Slide 50: Measuring equipment
How long does it take to measure?
The length of the reporting period depends on your objective:
If you want to control the efficiency => measurement forever.
If you want to report the savings results => measure until satisfied.
Requires costs for management and maintenance of measuring equipment
Choose wisely!

## Slide 51: Key issues
  Missing data
  Failed sensors
  Data collection systems that lose connection or power off
  Incorrect meter readings
  Lost electric bills
  Electricity companies that estimate meter readings
  ……………………..

## Slide 52: Key issues
M&V costs depend on M&V:
  Amount of required data and difficulty in obtaining good data
  Installation/maintenance of new meters
  Analysis of amount of required data
  Reporting format and frequency
  Length of reporting period
  Complexity of systems and energy saving solutions
  Required uncertainty
  Selected IPMVP option.
M&V budget should depend on:
  How much is the savings?
  How long is the payback period?
  How carefully will this project be researched?
  How much uncertainty can you accept?

## Slide 53: Key issues
Apply electricity prices to evaluate savings
Energy prices are complex and often change.
Use a full electricity price plan or carefully select an appropriate marginal price.
The ESCO contract should set a minimum price or may use an inflation factor.
The M&V plan should identify the energy price that will be used to evaluate savings and whether or how savings will be adjusted if prices change in the future.

## Slide 54: Key issues
Apply electricity prices to evaluate savings
CAREFUL!
Option C or D – To use a simplified single price, each month’s consumption must be the same price and must include all additional activities. It is safer to always use the full price structure.
Option A or B – Carefully choose the marginal price, possibly making some assumptions.

## Slide 55
Thank you!