## Slide 1
Module 11:
Energy efficiency in electrical systems and electric motors
Technical staffs
TRAINING PROGRAMME FOR INDUSTRIAL ENTERPRISES

## Slide 2: CASE STUDIES & DISCUSSION
Do you think your electrical system and electric motors in your company are efficient?
Please share a success story : Review industry cases where energy efficiency measures led to cost savings.
Failure Review: Discuss cases where inefficiencies persisted despite interventions.

## Slide 3
POWER QUALITY ASSESSMENT
Power Quality:
The term used to refer to the stability of voltage and frequency
Power quality: A set of limits on electrical parameters that allows the power system to operate most efficiently and ensures the longest lifespan of equipment
Power Quality Indicators:
Voltage
Frequency

## Slide 4
Issue | Effect on Equipment & Efficiency
Voltage Sags/Dips | Motors overheat, process interruptions, reset or trip of sensitive devices
Voltage Swells/Surges | Premature failure of lighting, control systems, and power supplies
Harmonics | Increased losses in transformers/motors, overheating, false tripping
Voltage Imbalance | Motor inefficiency, vibration, increased energy use, shortened lifespan
Frequency Variations | Timing errors in clocks, controllers, and sensitive electronics
Flicker | Lighting instability, operator discomfort, potential safety risks
Transients/Spikes | Damaged electronics, data loss, malfunction of digital systems
Poor Power Factor | Higher energy bills, need for oversized cables/equipment, energy waste
Effects of Poor Power Quality
POWER QUALITY ASSESSMENT

## Slide 5
PARAMETERS TO BE COLLECTED
Max, min, average operating power
Power factor (cosφ).
Phase balance
Harmonic distortion
Electricity consumption of each system, area.
It is necessary to install meters at the main distribution panels, main load lines, and large electricity-consuming loads...

## Slide 6
A low power factor causes negative economic and technical impacts, leading to voltage drops on transmission lines and power losses during transmission.
Power from 40 kW and above with a power factor cosφ < 0.9 must purchase reactive power according to Circular 15/2014/TT-BCT
REACTIVE POWER COMPENSATION
Power factor
Power factor
From 0.9 and above
Below 0.6

## Slide 7
Compensating reactive power ensures
=> Reduce electricity bill costs, ensuring economic and technical factors in the transmission system
Implementation method
Compensating power
Q = P*k.
Whereby
P (kW): power of the device
k: compensation factor
REACTIVE POWER COMPENSATION
Expected power factor
Current power factor

## Slide 8
Example of calculating economic efficiency
- The load power is 30 kW; the power factor is 0.7
- Energy bill cost is 252 million VND/year
- The power factor after compensation is 0.95
=> Compensation factor: k = 0,69
=> Compensating power
Q = 30 × 0,69 = 20,7 KVAr.
=> Compensation cost factor: k = 28,57%.
=> Savings in cost:
C = 252 x 28,57% = 72 million VND/year.
Circular 15/2014/TT-BCT dated May 28, 2014, of the Ministry of Industry and Trade
REACTIVE POWER COMPENSATION

## Slide 9: POWER FACTOR IMPROVEMENT
Qb = P.(tg1 – tg2)
tg1 : before compensation
tg2 : after compensation
What Is Reactive Power?
In AC systems, power consists of:
  Active (Real) Power (P, kW) – does useful work like turning motors.
  Reactive Power (Q, kvar) – supports magnetic fields in inductive loads (like motors, transformers), but does not perform useful work.
  Apparent Power (S, kVA) – combination of both.
Inductive loads (e.g., motors) consume reactive power, lowering the system’s power factor (PF) — the ratio of active to apparent power.
Capacitors generate reactive power (capacitive kvar) that cancels out the inductive reactive power.
Notes: Giới thiệu bảng tra dung lượng bù được cung cấp trong tài liệu học viên/ Introducing the compensation capacity lookup table provided in the delegates materials
Ví dụ: xí nghiệp có P = 0,9 MW; Q = 0,8 MVAr (ứng với cos = 0,75). Nếu đặt tụ nâng cos lên 0,95 thì sau bao lâu sẽ lấy được vốn? (biết Tmax = 4500 h). Giả sử là khi cos = (0,8-0,9) thì tiền điện là 700 đ/kWh, còn khi cos lớn hơn 0,9 thì giá tiền điện giảm 1% cho mỗi trị cos tăng 0,01 và ngược lại khi cos nhỏ hơn 0,9 thì giá tiền điện tăng 1% cho mỗi trị cos giảm 0,01
For example: an enterprise has P = 0.9 MW; Q = 0.8 MVAr (corresponding to cos = 0.75). If we set the capacitor to raise cos to 0.95, how long will it take to get the capital back? (know Tmax = 4500 h). Suppose that when cos = (0.8-0.9), the electricity bill is 700 VND/kWh, and when cos is greater than 0.9, the electricity price decreases by 1% for each 0.01 increase in cos And vice versa, when cos is less than 0.9, the electricity price increases by 1% for each decrease in cos of 0.01.
Dung lượng tụ cần đặt/ Capacitor capacity required:
QC = P(tg1 – tg2) với tg1, tg2 là tangen trước và sau khi bù
QC = P(tg1 – tg2) with tg1, tg2 being the tangen before and after compensation
QC = P(0,89 – 0,33) = 0,5 MVAr
Nếu lắp 2 bộ tụ 240 kVAr tổng số tiền đầu tư là: 26.460.000*2 = 52.920.000 đ
If installing 2 sets of 240 kVAr capacitors, the total investment amount is: 26,460,000*2 = 52,920,000 VND
Với hệ số cos = 0,75, giá tiền điện hiện tại là: 700đ (1 + 5%) = 735 đ/kWh
With the coefficient cos = 0.75, the current electricity price is: 700 VND (1 + 5%) = 735 VND/kWh
Nếu như nâng cos lên 0,95, giá điện là: 665 đ/kWh
If cos is raised to 0.95, the electricity price is: 665 VND/kWh
Với Tmax = 4500 h, số tiền phải trả trước khi đặt tụ trong một năm là
With Tmax = 4500 h, the amount to be paid before placing the capacitor for one year is
Z1 = 4500 * 0,9 * 1000 * 735 = 2.976.750.000 đ
Sau khi đặt tụ, số tiền điện phải trả trong năm là: (chưa tính giảm tổn thất)
After placing the capacitor, the amount of electricity to be paid during the year is: (excluding loss reduction)
Z2 = 4500* 0,9 * 1000* 665 = 2.693.250.000 đ
Thời gian hoàn vốn là hơn 2 tháng/ Payback period is more than 2 months.

## Slide 10: CAPACITOR INSTALLATION LOCATION
Centralized compensation:
Installed at the substation, only compensates the power factor (cosφ) for the transformer.
Advantages: Simple
Disadvantages: Only reduces electricity costs. Does not reduce transmission losses for the plant
Group compensation: Installed at the distribution panel in the plant's workshops.
Advantages: Reduces losses at the substation and wiring to the workshops.
Disadvantages: Does not reduce transmission losses for equipment, difficult to maintain and control.
Individual compensation:
Installed at the motor
Advantages: Reduces transmission losses on the power supply grid to the plant.
Disadvantages: Difficult to maintain and control
Notes: Giới thiệu bảng tra dung lượng bù được cung cấp trong tài liệu học viên/ Introducing the compensation capacity lookup table provided in the delegates materials
Ví dụ: xí nghiệp có P = 0,9 MW; Q = 0,8 MVAr (ứng với cos = 0,75). Nếu đặt tụ nâng cos lên 0,95 thì sau bao lâu sẽ lấy được vốn? (biết Tmax = 4500 h). Giả sử là khi cos = (0,8-0,9) thì tiền điện là 700 đ/kWh, còn khi cos lớn hơn 0,9 thì giá tiền điện giảm 1% cho mỗi trị cos tăng 0,01 và ngược lại khi cos nhỏ hơn 0,9 thì giá tiền điện tăng 1% cho mỗi trị cos giảm 0,01
For example: an enterprise has P = 0.9 MW; Q = 0.8 MVAr (corresponding to cos = 0.75). If we set the capacitor to raise cos to 0.95, how long will it take to get the capital back? (know Tmax = 4500 h). Suppose that when cos = (0.8-0.9), the electricity bill is 700 VND/kWh, and when cos is greater than 0.9, the electricity price decreases by 1% for each 0.01 increase in cos And vice versa, when cos is less than 0.9, the electricity price increases by 1% for each decrease in cos of 0.01.
Dung lượng tụ cần đặt/ Capacitor capacity required:
QC = P(tg1 – tg2) với tg1, tg2 là tangen trước và sau khi bù
QC = P(tg1 – tg2) with tg1, tg2 being the tangen before and after compensation
QC = P(0,89 – 0,33) = 0,5 MVAr
Nếu lắp 2 bộ tụ 240 kVAr tổng số tiền đầu tư là: 26.460.000*2 = 52.920.000 đ
If installing 2 sets of 240 kVAr capacitors, the total investment amount is: 26,460,000*2 = 52,920,000 VND
Với hệ số cos = 0,75, giá tiền điện hiện tại là: 700đ (1 + 5%) = 735 đ/kWh
With the coefficient cos = 0.75, the current electricity price is: 700 VND (1 + 5%) = 735 VND/kWh
Nếu như nâng cos lên 0,95, giá điện là: 665 đ/kWh
If cos is raised to 0.95, the electricity price is: 665 VND/kWh
Với Tmax = 4500 h, số tiền phải trả trước khi đặt tụ trong một năm là
With Tmax = 4500 h, the amount to be paid before placing the capacitor for one year is
Z1 = 4500 * 0,9 * 1000 * 735 = 2.976.750.000 đ
Sau khi đặt tụ, số tiền điện phải trả trong năm là: (chưa tính giảm tổn thất)
After placing the capacitor, the amount of electricity to be paid during the year is: (excluding loss reduction)
Z2 = 4500* 0,9 * 1000* 665 = 2.693.250.000 đ
Thời gian hoàn vốn là hơn 2 tháng/ Payback period is more than 2 months.

## Slide 11: STATIC VAR GENERATORS (SVG)
The SVG operates by determining the load current in real time through an externally mounted current transformer (CT) and determining the reactive component in the load current. The data is analyzed and then through the controller, the SVG adjusts the internal IGBTs using a pulse width modulation (PWM) signal so that the inverter generates a reactive current opposite to the reactive current of the load. This current is fed into the grid to compensate for the reactive component of the load current. By adjusting the voltage and phase angle or directly controlling the AC current, the SVG can consume or generate reactive power in accordance with the system demand or grid voltage
Notes: Giới thiệu bảng tra dung lượng bù được cung cấp trong tài liệu học viên/ Introducing the compensation capacity lookup table provided in the delegates materials
Ví dụ: xí nghiệp có P = 0,9 MW; Q = 0,8 MVAr (ứng với cos = 0,75). Nếu đặt tụ nâng cos lên 0,95 thì sau bao lâu sẽ lấy được vốn? (biết Tmax = 4500 h). Giả sử là khi cos = (0,8-0,9) thì tiền điện là 700 đ/kWh, còn khi cos lớn hơn 0,9 thì giá tiền điện giảm 1% cho mỗi trị cos tăng 0,01 và ngược lại khi cos nhỏ hơn 0,9 thì giá tiền điện tăng 1% cho mỗi trị cos giảm 0,01
For example: an enterprise has P = 0.9 MW; Q = 0.8 MVAr (corresponding to cos = 0.75). If we set the capacitor to raise cos to 0.95, how long will it take to get the capital back? (know Tmax = 4500 h). Suppose that when cos = (0.8-0.9), the electricity bill is 700 VND/kWh, and when cos is greater than 0.9, the electricity price decreases by 1% for each 0.01 increase in cos And vice versa, when cos is less than 0.9, the electricity price increases by 1% for each decrease in cos of 0.01.
Dung lượng tụ cần đặt/ Capacitor capacity required:
QC = P(tg1 – tg2) với tg1, tg2 là tangen trước và sau khi bù
QC = P(tg1 – tg2) with tg1, tg2 being the tangen before and after compensation
QC = P(0,89 – 0,33) = 0,5 MVAr
Nếu lắp 2 bộ tụ 240 kVAr tổng số tiền đầu tư là: 26.460.000*2 = 52.920.000 đ
If installing 2 sets of 240 kVAr capacitors, the total investment amount is: 26,460,000*2 = 52,920,000 VND
Với hệ số cos = 0,75, giá tiền điện hiện tại là: 700đ (1 + 5%) = 735 đ/kWh
With the coefficient cos = 0.75, the current electricity price is: 700 VND (1 + 5%) = 735 VND/kWh
Nếu như nâng cos lên 0,95, giá điện là: 665 đ/kWh
If cos is raised to 0.95, the electricity price is: 665 VND/kWh
Với Tmax = 4500 h, số tiền phải trả trước khi đặt tụ trong một năm là
With Tmax = 4500 h, the amount to be paid before placing the capacitor for one year is
Z1 = 4500 * 0,9 * 1000 * 735 = 2.976.750.000 đ
Sau khi đặt tụ, số tiền điện phải trả trong năm là: (chưa tính giảm tổn thất)
After placing the capacitor, the amount of electricity to be paid during the year is: (excluding loss reduction)
Z2 = 4500* 0,9 * 1000* 665 = 2.693.250.000 đ
Thời gian hoàn vốn là hơn 2 tháng/ Payback period is more than 2 months.

## Slide 12: STATIC VAR GENERATORS (SVG)
Notes: Giới thiệu bảng tra dung lượng bù được cung cấp trong tài liệu học viên/ Introducing the compensation capacity lookup table provided in the delegates materials
Ví dụ: xí nghiệp có P = 0,9 MW; Q = 0,8 MVAr (ứng với cos = 0,75). Nếu đặt tụ nâng cos lên 0,95 thì sau bao lâu sẽ lấy được vốn? (biết Tmax = 4500 h). Giả sử là khi cos = (0,8-0,9) thì tiền điện là 700 đ/kWh, còn khi cos lớn hơn 0,9 thì giá tiền điện giảm 1% cho mỗi trị cos tăng 0,01 và ngược lại khi cos nhỏ hơn 0,9 thì giá tiền điện tăng 1% cho mỗi trị cos giảm 0,01
For example: an enterprise has P = 0.9 MW; Q = 0.8 MVAr (corresponding to cos = 0.75). If we set the capacitor to raise cos to 0.95, how long will it take to get the capital back? (know Tmax = 4500 h). Suppose that when cos = (0.8-0.9), the electricity bill is 700 VND/kWh, and when cos is greater than 0.9, the electricity price decreases by 1% for each 0.01 increase in cos And vice versa, when cos is less than 0.9, the electricity price increases by 1% for each decrease in cos of 0.01.
Dung lượng tụ cần đặt/ Capacitor capacity required:
QC = P(tg1 – tg2) với tg1, tg2 là tangen trước và sau khi bù
QC = P(tg1 – tg2) with tg1, tg2 being the tangen before and after compensation
QC = P(0,89 – 0,33) = 0,5 MVAr
Nếu lắp 2 bộ tụ 240 kVAr tổng số tiền đầu tư là: 26.460.000*2 = 52.920.000 đ
If installing 2 sets of 240 kVAr capacitors, the total investment amount is: 26,460,000*2 = 52,920,000 VND
Với hệ số cos = 0,75, giá tiền điện hiện tại là: 700đ (1 + 5%) = 735 đ/kWh
With the coefficient cos = 0.75, the current electricity price is: 700 VND (1 + 5%) = 735 VND/kWh
Nếu như nâng cos lên 0,95, giá điện là: 665 đ/kWh
If cos is raised to 0.95, the electricity price is: 665 VND/kWh
Với Tmax = 4500 h, số tiền phải trả trước khi đặt tụ trong một năm là
With Tmax = 4500 h, the amount to be paid before placing the capacitor for one year is
Z1 = 4500 * 0,9 * 1000 * 735 = 2.976.750.000 đ
Sau khi đặt tụ, số tiền điện phải trả trong năm là: (chưa tính giảm tổn thất)
After placing the capacitor, the amount of electricity to be paid during the year is: (excluding loss reduction)
Z2 = 4500* 0,9 * 1000* 665 = 2.693.250.000 đ
Thời gian hoàn vốn là hơn 2 tháng/ Payback period is more than 2 months.

## Slide 13
    MINIMIZING HARMONICS
Definition of Harmonics (in Power Systems)
Harmonics are voltage or current waveforms in an electrical system that operate at integer multiples of the fundamental frequency (50 Hz in Vietnam, 60 Hz in some other countries).
The fundamental frequency is the standard sinusoidal waveform (e.g., 50 Hz).
Harmonics are distortions of this waveform and occur at:
  2nd harmonic: 100 Hz
  3rd harmonic: 150 Hz
  4th harmonic: 200 Hz
  ... and so on.

## Slide 14
Harmonics cause overload on the power lines and transformers; increase the system temperature and cause interference on the power grid; lead to overload in the electrical system.
When the total harmonic currents exceed the allowable limit, it can cause unexpected damage to machinery, delay operations, and pose a risk of fire and explosion, as well as energy losses.
fundamental frequency waveform
3rd harmonic
5nd harmonic
7rd harmonic
composite waveform
    MINIMIZING HARMONICS

## Slide 15
It is necessary to apply measures to reduce harmonics
Implementation method
Using harmonic filter reactors: This is the most widely trusted and used method
Using passive filters: There are two types, the zero-sequence filter and the active filter. The zero-sequence filter reduces or eliminates harmonic currents compatible with the transformer winding. Meanwhile, the active filter reduces harmonic currents by generating opposing harmonic waves
Using inverters with low harmonic waves
    MINIMIZING HARMONICS

## Slide 16
Economic efficiency
Reducing energy costs: Power quality improvement solutions can reduce heat, vibration, and noise in induction motors. As a result, energy costs decrease, and the efficiency of energy-consuming equipment improves.“
Extending equipment lifespan: The lifespan of equipment is also affected by poor power quality, leading to higher costs associated with maintenance and asset replacement
    MINIMIZING HARMONICS

## Slide 17
AHF - Active Harmonic Filter
When harmonic suppression is required, the operating circuit will measure and calculate the harmonic current spectrum using advanced algorithms programmed into the DSP. The processor will then determine the compensation current intensity corresponding to each harmonic level. The compensation current generation circuit will generate a control signal to the IGBT using the pulse modulation (PWM) method, thereby generating a current that is in phase with each harmonic level existing in the system. As a result, the harmonic current on the source side will be greatly reduce
    MINIMIZING HARMONICS

## Slide 18
AHF - Active Harmonic Filter
    MINIMIZING HARMONICS

## Slide 19: ELIMINATING CURRENT ON THE NEUTRAL LINE
Phase load balancing
Periodic measurement of neutral line current/phase current.
Measure at different times of the day

## Slide 20
Retail electricity prices for the manufacturing sector effective from May 4, 2023
Enterprises purchase electricity at the regulated three-tier tariff, including: peak hours, normal hours, and off-peak hours
Time frame
No
Electricity price
Voltage level from below 6 kV to below 22 kV
a) Normal hours
b) Off-peak hours
c) Peak hours
Voltage level below 6kV
a) Normal hours
b)Off-peak hours
c)Peak hours
LOAD MANAGEMENT

## Slide 21
Managing load operation to avoid peak hours => Reducing energy costs
Implementation method
Scheduling the operation of large-capacity equipment to avoid operating during peak hours with high electricity prices
Analyzing and reviewing the operation diagrams and processes to improve the load factor, thereby reducing the maximum demand
Temporarily shut down unnecessary loads when the maximum demand is approaching the established limit.
LOAD MANAGEMENT

## Slide 22
Monitoring a typical load
LOAD MANAGEMENT

## Slide 23
Example of calculating economic efficiency
Load capacity 100 kW at 0.4 kV voltage level
The reduced power capacity by shifting loads from peak to normal period is 30 kW
The reduced time: 4 hours/day during peak hours to shift operation to normal hours
=> The daily cost savings of the factory will be
C = 30 × 4 × (3.055 - 1.661) = 167.280 VND/day
LOAD MANAGEMENT

## Slide 24: How does your unit manage load to reduce energy costs during peak hours?
DISCUSS

## Slide 25
Your comments on the following electricity bill
DISCUSS

## Slide 26: OPPORTUNITIES FOR ELECTRICITY SAVINGS IN THE ELECTRICAL SYSTEM
Install the transformer near the load center to minimize transmission losses: The voltage drop from the transformer to the load is limited to a maximum of 2.5%
Identify the transformers operating under no-load conditions and redistribute the load: The transformer operates at its highest efficiency when the load is between 40-50%
Avoid phase imbalance: Voltage imbalance should be ≤1%, and current imbalance should be ≤10%.
Use transmission cables with appropriate cross-sectional area
Use an appropriate voltage level to avoid overvoltage or undervoltage: The optimal line voltage at the load should be between 370-390V
Regular maintenance: Check contact points to prevent phase loss...
Install an appropriate capacitor bank: The optimal power factor at the load is 0.95

## Slide 27: COMMON TYPES OF MOTORS
Squirrel cage rotor motor: Consists of multiple layers of steel stacked inside the core, along with evenly spaced copper or aluminum bars
Wound rotor motor: The steel core consists of electrical steel laminations similar to the stator. The winding is placed inside the rotor steel core

## Slide 28: MOTOR LIFECYCLE COST
Energy costs account for more than 80% of the total lifecycle cost of the motor. Therefore, optimizing motor usage will significantly reduce the operating costs of the motor
Chart: 
| Chi phí đầu tư ban đầu | Chi phí bảo dưỡng | Chi phí điện
 | 0.2 | 0.12 | 0.68

## Slide 29: BASIC PARAMETERS OF THE MOTOR
Motor speed (RPM): It is the rated speed of the motor
Frequency (Hz): In Vietnam, it is 50Hz
Number of poles of the motor: It is essentially the number of windings on the rotor, and the number of pole pairs is usually 2, 4, 6, or 8
Motor power (P) is the rated power of the motor, measured in kW or HP
Voltage U (V), Current I (A)

## Slide 30: BASIC PARAMETERS OF THE MOTOR
Power factor Cosφ: The motor's power factor can indicate whether the motor is operating under no-load, part-load, or full-load conditions
Motor load

## Slide 31: BASIC PARAMETERS OF THE MOTOR
Motor efficiency (h): It is a measure of the motor's ability to convert electrical energy into mechanical energy. In other words, it is the ratio of output mechanical power (Pout) to the input electrical power (Pin). Pout is usually listed on the motor's label
h = Pout/Pin
Reasons for reducing motor efficiency:
Motor repeatedly rewound.
Motor running under no-load conditions
Poor maintenance practices
Solutions to reduce motor losses :
Choosing a high-efficiency motor
Choosing a new motor
Do not rewind the old motor multiple times.

## Slide 32: OPPORTUNITIES FOR ENERGY EFFICIENCY IN ELECTRIC MOTORS
Choosing the right motor: Selecting a motor with a capacity larger than the requirement will reduce the motor's operating efficiency
The motor's efficiency significantly decreases when operating at 30-40% of its rated load (Low-load)
% full-load efficiency

## Slide 33: OPPORTUNITIES FOR ENERGY EFFICIENCY IN ELECTRIC MOTORS
Reducing the motor's no-load operating time
Consider replacing the motor when the load is less than 40% of the rated capacity
efficiency
load level
accept in the short term
acceptable operation
optimal
Level

## Slide 34: OPPORTUNITIES FOR ENERGY EFFICIENCY IN ELECTRIC MOTORS
Choosing high-efficiency motors: High-efficiency motors should be used in the following cases
Installing new equipment
There are significant adjustments to the production line
Investing in a backup motor
Instead of rewinding a damaged old motor, consider investing in a high-efficiency motor
High efficiency
Standard efficiency
Power(Hp)
Source:
Efficiency

## Slide 35: OPPORTUNITIES FOR ENERGY EFFICIENCY IN ELECTRIC MOTORS
Calculate when replacing from IE1 to IE3 for motor 75kW
Motor Efficiency Class | Efficiency (η)
IE1 | 93.0% (0.930)
IE3 | 95.4% (0.954)
1. Motor Efficiency Comparison
2. Input Power Required
Let’s calculate input power for each motor:
Output Power (Pₒ) = 75 kW
Input Power (Pᵢ) = Pₒ / η
Motor Class | Input Power (kW)
IE1 | 75 / 0.93 ≈ 80.65 kW
IE3 | 75 / 0.954 ≈ 78.61 kW
⇒ Savings per hour = 80.65 – 78.61 = 2.04 kWh
3. Annual Energy Saving
Assume operating time:
12 hours/day, 290 days/year = 3,480 hours/year
Then:
Annual savings = 2.04 × 3,480 ≈ 7,099 kWh/year
4. Cost Savings
Assume electricity price: 2,000 VND/kWh → 7,099 × 2,000 = ~14.2 triệu VND/year saved

## Slide 36: OPPORTUNITIES FOR ENERGY EFFICIENCY IN ELECTRIC MOTORS
QUESTION
1. Select and calculate the replacement for your Company's motor?
2. Find a quote for a high efficiency motor locally and calculate a simple payback period?

## Slide 37: OPPORTUNITIES FOR ENERGY EFFICIENCY IN ELECTRIC MOTORS
Using an inverter (or VFD) to control the motor speed: The inverter enhances energy efficiency by adjusting the motor's speed to match the variation in load
Inverters are most effectively applied in the following cases
When there is a need to change the speed/flow rate of the fluid: the system includes throttle valves and bypass valves
When the equipment's power is much larger than the required load current
The system has a flow controlled by periodic on/off cycles

## Slide 38: OPPORTUNITIES FOR ENERGY EFFICIENCY IN ELECTRIC MOTORS
Using direct drive
Energy savings: 5-15%

## Slide 39: OPPORTUNITIES FOR ENERGY EFFICIENCY IN ELECTRIC MOTORS
Periodic maintenance of electric motors
Monitoring the machine's sound
Checking the motor's temperature
Cleaning the exterior of the motor
Lubricating the bearings/shaft bearings
Measuring energy consumption
Scheduled maintenance according to the specified timetable.

## Slide 40
Động cơ 55 kW, hoạt động 20-40% công suất
Động cơ 37kW, kết hợp sử dụng biến tần
Giảm 63% điện năng tiêu thụ
    TYPICAL EXAMPLE
55 kW motor, operating at 20-40% power capacity
37 kW motor, combined with the use of an inverter-VFD
Reduce 63% of energy consumption
Notes: 40

## Slide 41: Factory A is using a transformer station with a rated capacity of 3,000 kVA. The current load of the station is 2,500 kVA. The current power factor at the transformer station is Cosφ = 0.80. The total losses under full load at the station are 3.5 kW, and the total installed capacity of the entire factory is Pdm = 4,000 kW. The factory plans to install capacitors to improve the power factor from Cosφ1 = 0.80 to Cosφ2 = 0.98. Calculate the required capacitor size and estimate the amount of CO2e reduction annually, given that the station operates 24 hours a day and 350 days a year, electricity price is 3,000 VND/kWh, and the estimated investment cost for each capacitor unit is 200,000 VND. The simultaneous factor is 80%. The load factor is 50%."
DISCUSS

## Slide 42
THANK YOU