## Slide 1
Module 13: ENERGY EFFICIENCY IN BOILERS AND STEAM SYSTEMS
TECHNICAL STAFFS
TRAINING PROGRAMME FOR INDUSTRIAL ENTERPRISEs

## Slide 2
CONTENT
Overview of fuel and combustion process
Overview of industrial boilers
Opportunity to save energy for boilers
Overview of steam distribution system
Energy saving opportunities for steam distribution systems
Application examples

## Slide 3
1. OVERVIEW OF FUEL AND COMBUSTION PROCESS

## Slide 4
The concept of fuel
Fuels are substances that, when burned, emit light and thermal energy. Fuel has 3 main forms including:
– Gaseous fuels (natural gas, companion gas, biogas, gas from gasification, etc.);
– Liquid fuel (DO oil, FO oil);
– Solid fuel (coal, firewood, rice husk, cashew shells and other agricultural by-products, etc.).
Fuel composition:
For solid fuel, the fuel composition is divided into:
– The Ultimate analysis has components C, H, S, O, N, ash, moisture whereby C, H, S are combustible components that generate heat and O, N are components in fuel that escape during combustion without generating heat.
– The Proximate analysis of the fuel has fixed carbon, volatile matter, ash, moisture, where by the ratio of each component affects the combustion characteristics of the fuel.
OVERVIEW OF FUEL AND COMBUSTION PROCESS

## Slide 5
  Ash level A:are the minerals remaining after fuel is burned. Ash abrades and stains heat-resistant surfaces, leading to a decrease in heat transfer coefficient. Ash is a harmful component in fuel.
  Humidity W(M):is the amount of water contained in the fuel. Their presence reduces combustion components and also consumes additional heat to evaporate moisture when fuel burns. It is a harmful ingredient in fuel.
  Volatile V:are gases such as CH4, hydrogen carbide, CO... are generated during pyrolysis in the early stages of the combustion process. The more volatile the fuel, the more flammable and exhausted it is.
Technological characteristics of fuel – significance

## Slide 6
Heating value of fuel : The Heating value of a fuel is the energy contained in 1 unit mass of fuel in kJ/kg; kCal/kg; Btu/lb etc. fuel calorific therapy is divided into: :
– High Heating value: Higher Heating Value (HHV) or Gross Calorific value (GCV) is a fuel thermotherapy that assumes that all the amount of steam formed during combustion is condensed and the amount of heat generated during that condensation is included in the Heating value.
– Low Heating Value (LHV) or Net Calorific Value (NCV) is fuel thermotherapy with the explanation that all the amount of steam formed during combustion is not condensed and that the amount of heat released by condensation is lost.
Fuel combustion process: Fuel combustion is a process where there is contact between the oxygen in the air and the combustible component of the fuel (C, H, O) to produce thermal energy with the following combustion reactions:
C + O2 = CO2
H2 + 1/2O2 = H2O
S + O2 = SO2
Technological characteristics of fuel – significance
Notes: Higher Heating Value – HHV hay Gross Calorific value – GCV
Lower Heating Value – LHV hay Net Calorific Value – NCV

## Slide 7
Theoretical air (stoichiometric air): is the amount of air theoretically required to completely burn one unit mass of solid or liquid fuel or one unit volume of fuel for gaseous fuel, (kg/kg of fuel, m3tc/kg of fuel).
Note: m3tc is a unit of volume calculated under standard conditions of 0 °C and 1 atmosphere whereby 1 mol = 22.4 liters or 1 kmol = 22.4 m3.
Actual air: The amount of air actually used during combustion because the ideal contact between oxygen in the air and the combustible component of the fuel cannot take place.
The combustion process therefore has the manifestation of an excess of air when the flue gas has the presence of oxygen components and at the same time there is a manifestation of lack of air in the presence of CO, H2, CxHy.
The determination of the theoretical amount of air and the actual air during combustion plays an important role in the selection of the air supply fan and flue gas exhaust fan, and it also plays an important role in evaluating the efficiency of fuel combustion.
Technological characteristics of fuel – significance

## Slide 8
Theoretical flue gas: is the amount of flue gas formed theoretically by the complete combustion of one unit mass of fuel for solid or liquid fuels or one unit volume for gaseous fuels. The composition of theoretical smoke includes(CO2 ,H2O, SO2 ,N2 ).
Actual flue gas: Is the actual amount of flue gas formed by combustion. The composition of actual flue gas may include: The composition of actual flue gas includes CO2, H2O, SO2, N2 just like in theoretical flue gas. However, some other components that may be present when analyzing flue gas include:
– Oxygen (O2) is a manifestation of the excess air composition necessary for combustion
– CO is a manifestation of incomplete combustion due to poor contact between oxygen and the combustion component of the fuel, improper temperature conditions or lack of air in the course of combustion.
Technological characteristics of fuel – significance
Notes: Thành phần của khói lý thuyết bao gồm:
– CO2 từ quá trình cháy thành phần carbon;
– H2O từ quá trình cháy thành phần Hydro và từ thành phần ẩm trong nhiên liệu và không khí;
– SO2 từ quá trình cháy thành phần S trong nhiên liệu
– N2 từ không khí

## Slide 9
Combustion and emission process
The combustion process of all types of fuel takes place with the participation of air.
The end product of combustion depends on the type of fuel burned.
  When burning gaseous fuels, the flame is naturally blue;
  When burning oil fuels, the flame is often yellow and produces smoke, due to the presence of CO and soot;
  When burning coal fuel, the flame is often straw yellow and bright.
  The efficiency of any fuel-using device depends on the efficiency of the combustion process;
  Quantity theoretical atmosphereis the amount of air Minimum required to completely burn 1 kg of fuel or 1 Nm3gas;
  In reality, the amount of air supplied to the combustion process must always be greater than the theoretical amount by a certain margin, known as excess air.

## Slide 10
Combustion - Excess air and its meaning
Maintaining this excess air (residual air) will determine the efficiency of the combustion process. The amount of excess air that achieves the highest combustion efficiency is called the optimal amount of excess air.
The optimal amount of excess (excess) air depends on the fuel type and combustion type.
The amount of excess air that exceeds or falls below the optimal level will reduce the efficiency of the combustion process.
Excess air coefficient:is the ratio between the actual amount of air supplied (Vttkk) with the calculated theoretical amount of air denoted α, accordingly we have:
Excess air coefficient
 = Vkk / Vokk
Determination formula operate
 operate = 21/(21 – O2)
 operate ≈ CO2max /CO2

## Slide 11
Excess air coefficient 
Fuel | Optimal
Gas, Oil DO | 1,05 ÷ 1,15
FO oil | 1,10 ÷ 1,25
Charcoal (burn on grate) | 1,3 ÷ 1,5
Firewood, rice husk | 1,5 ÷ 1,6
Combustion - Excess air and its meaning
Select  optimal

## Slide 12
Fuel selection criteria
Choosing the right type of fuel is very important. This will depend mainly on their cost.
Each fuel has a different characteristic and also has a different price structure.
To make it easier to compare fuels, a common term is “heat costs”
Coal has the lowest thermal cost of all fuels. Therefore, coal is often chosen in places where fuel use intensity is high (about more than 10 tons/day).

## Slide 13
Q&A
Do you have any concern or question regarding boilers and steam system in your work?

## Slide 14
2. OVERVIEW OF BOILER

## Slide 15
Concept of boiler
The concept of an industrial boiler refers to a closed vessel system used in industrial settings to generate steam for various processes. It works by heating water using a fuel source—such as natural gas, oil, coal, or biomass—so that the resulting steam can be used for:
Heating
Power generation
Industrial processes (like drying, cooking, distillation, etc.)
Key Features:
Core component of steam systems used in many industries (e.g., food, textile, chemical, and energy).
Works under pressure and must be carefully designed, operated, and maintained for safety and efficiency.
Typically part of a larger steam system, including steam distribution, producer, usage, and condensate return.
Distribution
Producer
Usage
Recovery
Figure 1: Conventional Steam System (Source: US DOE Steam System Best Practices Program – Steam System Sourcebook)

## Slide 16
Classification of boilers
According to fuel used
According to installation layout
According toThe structure of the system receives heat and generates steam
Other classifications (capacity, steam parameters,...)

## Slide 17
Fire tube boiler
Advantage :
  The structure is simple, easy to manufacture, and the price is not high.
  Quick installation. Easy to use
  Cleaning & repairing fire pipes is not difficult.
  Large water volume: stable pressure
  Requires moderate water quality
Weakness:
  Not suitable for solid fuel
  Capacity and pressure are limited
  Poor water circulation in the furnace
  Slow startup
  Easily damaged fire tube and sieve surface when water is depleted or crusted
Fire tube boiler
Classification according to the method of receiving heat to generate steam

## Slide 18
Water tube boiler
Advantage :
  High operating pressure
  High steam generation efficiency.
  Rapid steam production
  Safer at high pressure
  Easily integrated with automation systems
  Modular design possible
Weakness:
  High initial investment cost
  More complex operation and maintenance
  Strict feedwater quality requirements
  Longer installation time (for large units)
Water tube boiler
Classification according to the method of receiving heat to generate steam

## Slide 19
Classification according to the method of combustion and the structure of the fire chamber
Fixed grate boiler: The boiler has a combustion chamber structure with a fixed grate that allows fuel to be supplied on the grate surface, wind is supplied from under the grate for fuel combustion.
1. Boiler door; 2. Grating wings; 3. Side burner; 4. Fire chamber space; 5. Roll boiler; 6. Air distribution chamber; 7. Air ducts; 8. Funnel ash slag; 9. Slag waste hole
Fixed recorders joined by registers
Fixed burn chamber
Notes: The fixed grate boiler has a simple structure, however, it has many disadvantages that lead to heavy labor in feeding, coal removal, and cement discharge, and cannot increase capacity.
Many mechanized structures are introduced such as flip grate structure, ladder grate structure and movable ladder to help increase furnace capacity and reduce heavy labor.

## Slide 20
Chain grate boiler: A type of boiler with a combustion chamber with a movable chain grate whereby fuel can be fed into the hopper from one side of the chain grate and recorded in motion into the combustion chamber. The moving process allows the fuel to burn out when it exits the combustion chamber.
Chain grate boiler
Classification according to the method of combustion and the structure of the fire chamber

## Slide 21
Fluidized bed boiler:
A type of fuel boiler with small particle size and high uniformity. The boiler has a recording structure with wind fungi that make it possible to blow the wind up at high speed causing the fuel to be blown away suspended in the combustion chamber called fluidization mode. For a stable boiling mode and temperature in the combustion chamber, an amount of inert particles in the form of sand, small particulate slag can be introduced and maintained in it besides fueling.
Fluidized bed boilers have great advantages of multi-fuel combustion, high combustion efficiency with low excess air coefficient, low combustion chamber temperature (840 – 900 oC) to help reduce NOx emissions.
Fluidized bed boiler
Classification according to the method of combustion and the structure of the fire chamber

## Slide 22
Boiler selection
Oven a little bit tube fire | Burning oil and gas Burn coal and firewood | Small and medium capacity 3-shift operating mode HT uses steam: large equipment
Oven a little bit tube water stand | Burn DO oil and gas | Labour capacity small Are not luck onion3 cases HThistory use a little bit:much set bag small,need a little bit fast
Curved water tube boiler with steam drum | Burn all types of fuel Very suitable for solid materials | Medium and large capacity 3-shift operating mode HT uses steam: large equipment requires high pressure, superheated steam
Question: How is a fire tube boiler different from a water tube boiler?
1. fire tube boiler with water flowing in the tube; smoke outside the tube, but the opposite is true for water tube boilers
2. Fire tube furnace tube boiler has water outside the tube; smoke inside the tube while water tube boilers do the opposite.
3. Fire tube boiler is a boiler that burns fire in the tube while water tube boiler puts water in the tube.

## Slide 23
Technical specifications of the boiler
p : pressure [kG/cm2 ; at; bar; MPa]
t : temperature [oC] – (temperature of superheated steam)
D : Rated steam output [kg/h; t/h; BHP]
Rated steam output (D) : is the largest output that the boiler can achieve, ensuring long-term, stable operation with given steam parameters without destroying or adversely affecting the working mode of the boiler
  Maximum steam output (Dmax): is the largest steam output that a boiler can produce, but only for a short period of time, meaning that the boiler cannot work for long with maximum steam output. Dmax = (1.1 ÷ 1.2)D
  Economical steam output (DKT): is the steam output in which the boiler works with the highest economic efficiency. Economical steam output is equal to: Dkt = (0.8 ÷ 0.9)D

## Slide 24
Heat Balance and Determination of Boiler Efficiency
According to TCVN 8630-2019 boiler – energy efficiency and determination method, the energy efficiency level of boilers is 5 levels. Where:
  – Level 1: energy saving level of class 1.
  – Level 2: energy saving level 2.
  – Level 3: the minimum level applies to new boilers and no more than 2 years of operation.
  – Level 4: the minimum applicable to boilers that have been operating for more than 2 years to less than 10 years.
  – Level 5: the minimum applicable to boilers that have been operating for 10 years or more.

## Slide 25
Heat balance in the boiler
Qđv = Qcó ích + Losses
Qđv = Q1 + Q2 + Q3 + Q4 + Q5 + Q6
Thermal performance
ηt = Q1 / Qđv = q1 (positive balance)
= 100 – (q2 + q3 + q4 + q5 + q6), % (negative balance)
In there
  Q1 = D(ih – inc) Qđv = BQth
D is the output of steam (kg/h); steam and inc are the enthalpy of steam and water respectively grade (kJ/kg); B is the amount of fuel consumed per hour (kg/h); Qtlv is the working low calorific value (kJ/kg).
Qđv is the amount of heat caused by 1 kg of solid or liquid fuel or 1m3tc of gaseous fuel burned and supplied to the boiler;
Q1 is the amount of heat used to generate steam (kJ/kg, kJ/m3tc);
Heat Balance and Determination of Boiler Efficiency:
Notes: Giải thích cho học viên về các ký hiệu:
  Q : Nhiệt lượng (kJ/kg, kJ/m3tc)
  Qđv : Nhiệt lượng đưa vào (kJ/kg, kJ/m3tc)
  q : nhiệt lượng tính theo giá trị tương đối (%):
  q1 + q2 + q3 + q4 + q5 + q6 = 1 hay 100 %
  ih : entanpi của hơi
  inc : entanpi của nước cấp
  B : tiêu hao nhiên
  D : sản lượng hơi
Nêu rõ ý nghĩa & phạm vi sử dụng của phương pháp xác định hiệu suất lò hơi theo cân bằng thuận và cân bằng nghịch
Giải thích thêm về công thức Q1 = D(ih – inc)
  ih - entanpi của hơi: nhiệt lượng nằm trong 1 kg hơi
  inc - entanpi của nước cấp: nhiệt lượng nằm trong 1kg nước cấp
  (ih – inc) - nhiệt lượng cần để chuyển 1kg nước thành 1 kg hơi
  D(ih – inc) - nhiệt lượng cần chuyển D kg nước thành hơi

## Slide 26
Types of losses in boilers
Q2 is the amount of heat loss caused by flue gas carried outside the boiler (kJ/kg, kJ/m3tc);
Q3 is the amount of heat loss due to chemically incomplete combustion (kJ/kg, kJ/ m3tc);
Q4 is the amount of heat loss due to unburned carbon in ash (kJ/kg, kJ/ m3tc);
Q5 is the amount of heat loss due to heat dissipation from the exterior of the boiler wall to the surrounding air (kJ/kg, kJ/ m3tc);
Q6 is the amount of heat loss brought out by hot slag ash (kJ/kg, kJ/m3tc).
q2 losses depend on the exhaust flue gas temperature and fluctuate between 4 ÷ 7% depending on the type of boiler and fuel quality.
q3 value is determined through the CO composition and is usually small (normally about 0 ÷ 1.5%) and will increase significantly when operating in poor combustion mode.
Loss q4 is characterized by the appearance of non-combustible substances in solid form, which depend on the substance amount of fuel and combustion chamber structure. For powdered coal boilers, q4 ranges from 0.5 ÷ 5%.
q5 depends on the surface area outside the boiler and the temperature difference between the boiler surface and the surrounding air. The q5 value is usually not large, in the range from 0.2 to 0.5%.
q6 is not large, about 0.5 ÷ 2% when burning solid fuel and discharging liquid slag. When discharging slag ash in solid form, the q6 loss is only calculated when the ash content of the fuel is high.
Notes: Giải thích về các loại tổn thất:
  q2 : Tổn thất do phần nhiệt khói thải mang ra ngoài.
  q3 : Trong khói thải vẫn còn những chất khí cháy không hoàn toàn
  q4 : Một phần nhiên liệu cháy không kịp bị thải ra ngoài
    + Cỡ hạt than không đều, hạt nhỏ - bị lọt, cục lớn - cháy không hết lõi than
    + Cấu tạo ghi lò: khe hở của ghi lớn hơn cỡ hạt than
    + Ghi bị cong vênh
    + Xúc xỉ có lẫn than ra khỏi buồng đốt
  q5 : Do vách nồi hơi có nhiệt độ cao hơn không khí xung quanh- do bọc cách nhiệt không tốt
  q6 : Lượng nhiệt do xỉ thải mang ra ngoài
    + Lượng tro nhiều (tạo xỉ)
    + Nhiệt độ xỉ cao
Đặt câu hỏi, yêu cầu học viên cho biết loại tổn thất nào là lớn nhất trong lò hơi. Trả lời: q2 và q4
Đốt dầu hay khí : q4 và q6 = 0
Đốt than thủ công : rất khó kiểm soát lượng không khí và nhiên liệu => tổn thất q2 và q3 tăng cao => Hiệu suất lò thấp
Lưu ý: q2, q3 , q4 sẽ được giải thích thêm ở slide sau, ở slide này chỉ giải thích chi tiết hơn về q5, q6

## Slide 27
3. OPPORTUNITIES TO EE FOR BOILER

## Slide 28
Minimize excess air.
Install heat recovery equipment.
Clean the heat transfer surface of the boiler.
Improve water treatment.
Install an automatic oven discharge controller to minimize oven exhaust.
Heat recovery from boiler exhaust.
Add or restore boiler refractory.
Investigate opportunities for fuel conversion.
OPPORTUNITIES TO SAVE ENERGY FOR BOILER

## Slide 29
1. Minimize excess air
Goal: Reduce excess air in combustion to avoid heat loss and improve efficiency.
Why: Actual air use often exceeds theoretical needs → extra air increases heat loss.
Control Basis: Adjust fuel flow based on steam pressure; manage air-fuel ratio.
Control Methods:
Positioning Control
  Mechanical link between fuel and air flow devices.
  Periodic oxygen & combustion measurements.
  Manual adjustments maintain air-fuel relationship.
Automatic Control
  Fuel flow valve + flue gas oxygen monitor.
  Continuous exhaust oxygen measurement.
  Adjusts air based on combustion curve automatically.
  More efficient than positioning; saves more energy with VSD fans.
Key Benefit: Efficient combustion → less heat loss, lower fuel use, and energy savings.

## Slide 30
2. Install exhaust heat recovery equipment
Description: Heat recovery equipment captures waste heat from boiler exhaust gases or blowdown water and reuses it for preheating boiler feedwater, combustion air, or process fluids. By recovering this otherwise wasted thermal energy, the system reduces fuel consumption, improves overall boiler efficiency, and lowers greenhouse gas emissions. This not only cuts operating costs but also supports sustainability goals.
Key Benefits:
Reduce fuel consumption by up to 10–20% depending on system design.
Extend equipment life through reduced thermal stress.
Lower CO₂ emissions and improve environmental performance.
Example: Economizers installed on flue gas outlets can preheat feedwater, while flash steam recovery systems can reuse heat from boiler blowdown.

## Slide 31
3. Cleaning the heat transfer surfaces of the boiler
Over time, heat transfer surfaces become soiled.
Adhesion on the heat transfer surface results in a decrease in heat transfer capacity and an increase in the flue gas temperature lower boiler efficiency a planned and preventive service procedure is required to periodically clean the heat transfer surfaces in the boiler

## Slide 32
4. Improving water treatment
Feed water quality is most affected by the composition of the treated water. Condensate is usually the cleanest water in a steam system. Supplemental water must be treated before being added to the system. When the water treatment system is improved, the quality of the feed water can be improved.
Boiler supplemental water must be treated appropriately based on the water chemistry mandate for reliable boiler operation.
Flush management depends on two factors: boiler operating pressure and water treatment.
When the best supplemental water quality is ensured, the amount of bottom discharge required will be reduced.

## Slide 33
5. Installing an Automatic Oven Discharge Controller in Boiler Systems
Purpose: Reduces excess heat and steam loss by automatically regulating oven exhaust flow.
How It Works:
  Monitors oven temperature and pressure in real-time.
  Adjusts discharge dampers automatically for optimal operation.
Benefits:
  Energy Savings: Cuts unnecessary heat loss → lowers fuel consumption by 5–15%.
  Improved Efficiency: Maintains stable oven temperature for better product quality.
  Reduced Emissions: Less fuel burned → lower CO₂ and pollutant output.
  Lower Operating Costs: Minimizes manual adjustments and heat waste.
Implementation Considerations:
  Integration with existing control systems.
  Staff training for monitoring and maintenance.

## Slide 34
6. Heat recovery from boiler exhaust
Much of the energy lost during boiler discharge can be recovered using a combination of the following two methods:
  – Flash steam recovery;
  – Feed water preheat.
High-pressure furnace discharge water is fed into an accumulator that operates at a low pressure (usually slightly above the deaerator pressure).
Part of the bottom discharge liquid converts to steam at a lower pressure, which is flash steam. This flash steam is clean and can supply low pressure steam distribution head or supply steam to deaerator or feed water heating system.
Boiler Exhaust Heat Recovery
The liquid remains in the pressure expansion tank at saturation temperature (> 100 °C) and can still be used to preheat the supplemental water in the heat exchanger.

## Slide 35
7. Add or restore boiler refractories
Boiler insulation and refractory materials are intended to ensure the safety of plant personnel and reduce shell loss due to radiation and convection.
External surfaces may need periodic repair due to ambient conditions or damage during operation.
In addition, during the annual inspection, the refractory materials must be inspected for any damage, cracks and breaks. Thermal cycling or direct impact of hot material can lead to incident in the refractory material.
As such, tasks such as maintenance, prediction, and prevention are needed for reliable steam system operations. Plant personnel should use infrared thermal cameras to look for hot spots (temperature > 70 °C) and compare these images over time to see if repairs are needed.

## Slide 36
8. Investigate opportunities for fuel conversion.
Fuel selection can affect operating costs due to differences in energy prices and boiler efficiency.
Fuel efficiency is generally an influencing factor when changing fuels. The benefits to fuel conversion can include fuel costs, operating costs, in addition, environmental concerns can also be a significant concern associated with fuel change option.
Fuel conversion does not necessarily mean "complete" fuel conversion. Industrial steam plants can have multiple boilers in operation and fuel conversion can also be applied in the following directions:
  – Turn off the boiler operating with a certain type of fuel.
  – Reduce the steam output of boiler A working with fuel type 1 and correspondingly increase the output of boiler B working with fuel type 2.
  – Simultaneous combustion of multiple fuels for the boiler and change the fuel burning ratio.

## Slide 37
4. OVERVIEW OF STEAM DISTRIBUTION SYSTEM

## Slide 38
The steam distribution system consists of all main pipes, branch pipes, valve systems, steam traps, etc., in order to transport steam from the steam production location to the steam consumption location.
Typical Steam System
A general steam system has four primary areas:
  – Production.
  – Distribution.
  – End use and/or cogeneration.
  – Condensate recovery.
Typical Steam System
Notes: Trong đó, khu vực sản xuất bao gồm:
– Lò hơi.
– Các thiết bị phụ trợ lò hơi (bơm, quạt, điều khiển,...).
– Bộ tiết kiệm.
– Bộ gia nhiệt trước không khí.
– Thiết bị xử lý nước.
– Thiết bị khử khí.
– Bơm nước cấp.
– Thiết bị xử lý và dự trữ nhiên liệu.
Khu vực phân phối hơi là một phần của hệ thống hơi, bao gồm những thành phần chính như sau:
– Các đường ống.
– Các trạm hoặc van giảm áp.
– Các chân góp giọt nước ngưng (drip legs).
– Bộ tích hơi nước.
– Thiết bị giảm nhiệt độ hơi quá nhiệt.
Khu vực sử dụng cuối cùng bao gồm các thiết bị chính:
– Bộ trao đổi nhiệt.
– Cột cất.
– Thiết bị bay hơi.
– Bếp nấu.
– Máy sấy.
– Thiết bị sưởi ấm.
– Tuabin hơi.
Khu vực thu hồi nước ngưng bao gồm các thiết bị chính:
– Các bẫy hơi.
– Các bể chứa thu gom nước ngưng.
– Các bơm nước ngưng.
– Các đường ống nước ngưng.

## Slide 39
Important components of the steam distribution system:
Pipeline
Condensate drainage point
Steam extraction lines
Coarse filter
Fine filter
Split trap
Steam trap
Ventilatory
Condensate recovery system
Insulation
Question: What is the function of the steam accumulator in the steam system?
1. Reserve steam for variable load operations
2. Recover steam generated from furnace discharge water or high pressure condensate.
3. To store recovered condensate.

## Slide 40
Pipe system
The steam pipeline system is designed and selected in accordance with safety and technical requirements to ensure the most efficient distribution of steam.
Steam distribution pipe system
Pipe material: Carbon steel or copper
Proper pipe size is very important
Pipeline size is too large:
  Expensive materials and installation costs
  Enhances the formation of condensate in pipes
Pipeline size too small:
  Low pressure at the site of use
  Risk due to lack of breath
  Risks from corrosion, hydraulic shock, and noise
Calculate pipe size: Based on pressure drop or steam flow rate

## Slide 41
Valve system
The valve is an essential component of the steam pipeline, as it regulates the pressure in the steam distribution pipe systems and facilitates the maintenance and repair process.
Globe valve
Gate valve
Some types of steam valves

## Slide 42
Steam trap
Steam traps are responsible for discharging condensate and gas from steam pipelines and other equipment that uses steam without allowing steam to escape.
Steam traps are frequently neglected due to the lack of resources and expertise of plant maintenance teams, as well as their ignorance of steam traps and their operation.
Steam traps serve several crucial operational functions for a steam system, but the most crucial are as follows:
  – They allow air and large quantities of condensate to escape during start-up process.
  – They allow collected condensate to enter the condensate return system during normal operation, while minimizing (or eliminating) steam loss.
Have three most common types in use today are as follows:
  – Bucket type steam trap.
  – Ball float type steam trap.
  – Thermodynamic steam trap.

## Slide 43
Bucket type steam trap
Structure of the float cup type steam trap
The working principle of a bucket type steam trap
Notes: The float cup steam trap, also known as the island bucket type, is made up of the following major components:
– Trap body.
– Input and output: connected to the pipeline system.
– Bucket (inverted).
– Vent: The top of the beaker was chiseled to allow air and vapor to escape into the trap.
In bucket type steam traps, the bucket is connected to a lever that opens and closes the trap valve in response to the bucket’s movement. When air or steam flows into the bottom of the float cup, the cup floats. In this position, the float cup closes off the air outlet.
The vent on the top of the bucket permits a small amount of steam to escape to the trap's top. As steam escapes through the vent, condensate fills the interior of the cup, causing the cup to gradually sink and allowing the lever to open the trap valve and release the condensate (along with the steam being held in the trap).

## Slide 44
Ball float-type steam trap
Structure of Ball float-type steam trap
The working principle of a balloon-type steam trap
Notes: Balloon-type steam trap consists of the following primary components:
– Trap body.
– Inlet (steam) and outlet (condensate).
– Floating balloon.
– Vent.
The working principle of Ball float-type steam trap is as follows:
When hot steam and condensate enter the steam trap, the gas will escape through the air outlet, the condensate will condense and gradually rise, and the float ball, along with the shafts and levers, will lift the plug from its initial position, allowing condensate to escape.
When condensate is released, the amount of condensate in the trap tank decreases to a low level, causing the float ball to return to its original position and the valve discharge hole to close. The process is ongoing and contributes to keeping the steam system as dry as possible

## Slide 45
Thermodynamic steam trap
Structure of thermodynamic steam trap.
The working principle of thermodynamic steam trap
Notes: Thermodynamic steam trap (or coin type) is a type of condensate collection trap that contains a disc in the shape of a coin and is made up of the following components:
– Valve disc (or coin).
– Trap body.
– Filter.
– Inlet (steam), outlet (condensate).
The thermodynamic steam trap is a type of steam trap that operates due to the dynamic effect of steam and condensate passing through the trap. In this steam trap, the valve disc moves up and down based on gravity and the steam pressure within the trap, which rests on a flat surface inside the trap's lid.
When the system collects sufficient condensate to increase the pressure beneath the valve disc, the disc is pushed to the top of the lid. The condensate and air then exit through the outlet of the steam trap (outlet). When the condensate has been drained from the trap, according to the trap's inlet, additional steam enters at a high velocity and moves to the top of the plate, creating a pressure zone. The low bottom of the disc combined with the disc's gravity will cause the valve disc to descend, closing the outlet position and preventing steam from escaping.

## Slide 46
5. EE OPPORTUNITIES FOR STEAM DISTRIBUTION SYSTEMS

## Slide 47
Some of the key solutions to reduce losses in steam distribution systems include:
  Steam leak control.
  Check the steam pipe insulation.
  Control steam pipeline design.
  Condensate recovery.
  Recovery of flash steam.
Types of losses on the steam distribution system
EE OPPORTUNITIES FOR STEAM DISTRIBUTION SYSTEMS

## Slide 48
1. Steam leak control
Locations where steam leaks often occur:
  – Flanges and gasket joints.
  – Pipe joints.
  – Valve, body and packaging.
  – Steam trap.
  – Pressure reducing valve.
  – Pipeline errors.
A regular maintenance program that finds and eliminates steam leaks is essential to the efficient operation of a steam system.
Amount of steam leaking through the leak.
Steam loss according to pressure
Steam pressure (kg/cm2) | Leak hole diameter (mm) | Leakage steam loss (kg/h)
3,5 | 3,12 | 18
 | 6,25 | 72
 | 12,5 | 287,9
5,5 | 3,12 | 25,5
 | 6,25 | 102,1
 | 12,5 | 408,3
15 | 3,12 | 59,7
 | 6,25 | 238,7
 | 12,5 | 954,9
42 | 3,12 | 151,1
 | 6,25 | 604,4
 | 12,5 | 2417,4
Notes: Steam trap incidents also account for a large portion of steam leaks in industrial plants. In general, steam trap incidents are more difficult to observe than piping incidents, especially in closed condensate systems.

## Slide 49
1. Steam leaks from pipes and steam valves
For example:
- Steam pressure 10 bar
- Hole diameter: 6.4 mm
- Steam price: 20US$/1,000 kg of steam
- Operating time: 7,500 hours/year
 Annual cost due to steam loss: 18,000 US$/year
Pat,Can not see steam leak
800 Liter/year
There was a roar
2,000 - 4,000 Liter/year
See a slight leak
There was a roar,See the line slightly leaking

## Slide 50
  2. Check the steam pipe insulation.
Insulation needs to be done through regular maintenance, inspection and assessment in all industrial plants. Insulation is important for steam systems due to the following number of reasons:
  – Ensure the safety of workers in the plant.
  – Minimize energy loss.
  – Maintain steam conditions for required end use.
  – Protect equipment, pipes from ambient conditions.
  – Maintain the integrity of the steam distribution system.
The most common areas where insulation is often lacking or damaged include::
  – Steam distribution manifolds.
  – Valve.
  – End-use devices.
  – Steam storage pools and tanks.
  – Recovery lines.
Notes: Một số lý do dẫn đến lớp bảo ôn bị thiếu hoặc hỏng, bao gồm:
– Thiếu lớp cách nhiệt do các hoạt động bảo trì.
– Bảo ôn bị hỏng do sự cố.
– Sự hao mòn bình thường của lớp bảo ôn do điều kiện môi trường xung quanh.
– Van và các thành phần khác không được cách nhiệt trong thiết kế.

## Slide 51
Type tube | Heat loss (W/m) (t : 150oC) | 
 | Uninsulated pipes | Insulated pipes (50mm)
100 mm | 770 | 115
150 mm | 1250 | 170
200 mm | 1440 | 195
Loss of bare pipe, diameter 89 mm, black steel, surface temperature 90 oC
No insulation
320 W/m
Insulation thickness 50 mm
29 W/m
Insulation thickness 100 mm
19 W/m
Radiant heat loss can be calculated using the following simple formula:
TTbx = [10 + (t1 – t2) / 20] × (t1 – t2); (kcal/hour/m2)
In which:
+ t1 is the surface temperature of the pipe, oC.
+ t2 is the ambient temperature, oC.
50 mm insulation compared to bare pipes: 320 - 29 = 291 W/m Save 263 liters of oil/year
50 mm insulation compared to 100 mm insulation: 29 - 19 = 10 W/m Additional cost of 9 liters of oil/year
  2. Check the steam pipe insulation.

## Slide 52
  3. Control steam pipeline design.
Energy auditors need to evaluate steam pipelines based on several factors:
  – Pipe material is: steel, plastic, etc.
  – Whether the pipe size is suitable or not: If the pipe cross–section is too small, it will lead to a large pressure loss.
  – Pipe layout ensures slope: If the pipe is 100m long, the average slope is 1 m.
  – Arrange to install steam traps on pipes reasonably: corresponding to 30 – 50 m pipeline, there is a steam trap, behind each manifold or in front of the valve, a steam trap is required, etc.
Suitable slope of the pipe

## Slide 53
4. Condensate recovery
When condensate is not returned to the system, the system suffers from heat loss. Since the condensate recovered is usually at high temperature and is clean, condensate recovery saves fuel costs as well as water treatment costs.
Condensate recovery system
Saving rate when recovering condensate
50 % returned
100 % returned
For every 6OC rise in boiler feed water temperature, there is a 1 % raise in boiler efficiency

## Slide 54
5. Flash steam recovery
USE::
- Heat supply for heat exchange equipment
- Warm up boiler feed water
Ratio of flash steam generated from condensate

## Slide 55
For example: Medium-pressure condensate at 10 bar saturation is fed into a pressure expansion steam vessel operating at 3 bar (Figure 8.26). This condensate flow is estimated to be 15 T/h. Assuming steady state operation, steady flow.
Calculate the amount of flash steam generated in a 3 bar pressure vessel?
Flash steam recovery
5. Flash steam recovery

## Slide 56
For example:
We have, the ratio of flash steam generated is calculated by the formula:
5. Flash steam recovery
With the enthalpy values (look up the steam table) are:
– Condensate (10 bar, saturated condition): icondensate, 10 bar = 781.5 kJ/kg.
– Condensate (3 bar, saturated condition): icondensate, 3 bar = 605.3 kJ/kg.
– Steam (3 bar, saturated conditions): isteam, 3 bar = 2,738.6 kJ/kg.
Substituting into the above equation we have; the flash steam ratio produces:
So, the amount of flash steam produced:
= 0.0826 ×15=1.25 T/h

## Slide 57
Q & A
Do you have any question in operation and maintain of boilers and steam in your factory?

## Slide 58
THANK YOU