## Slide 1
Module 6:
Efficient operation and maintenance of energy-using equipment
Technical staffs
TRAINING PROGRAMME FOR INDUSTRIAL ENTERPRISES

## Slide 2: OBJECTIVES
Understand principles and characteristics of operating industrial equipment
Identify main energy-consuming systems
Detect energy waste signals during operation
Master key issues in effective operation and maintenance of energy-using equipment

## Slide 3
PART 1: OVERVIEW

## Slide 4: OVERVIEW OF ENERGY USE IN INDUSTRY
Energy consumption in factories:
Thermal (40–60%)
Electricity (30–50%)
Other auxiliary fuels
Key systems:
Steam (Boiler, distribution network)
Cooling (Chiller)
Compressed air (Air compressors)
Fans, pumps, motors, lighting

## Slide 5: FACTORY ENERGY OVERVIEW DIAGRAM

## Slide 6: CLASSIFICATION OF MAIN ENERGY CONSUMPTION SYSTEMS
Thermal systems: boilers, heat exchangers, dryers
Cooling systems: chillers, cooling towers
Compressed air systems: compressors, air tanks, pipelines
Electric motors: fans, pumps, conveyors
Lighting, auxiliary heating equipment

## Slide 7: IMPACT OF IMPROPER OPERATION ON ENERGY CONSUMPTION
Improper operation and poor maintenance may reduce the operational life of the equipment.
Operating at incorrect load causes waste in electricity/steam
Non-optimized pressure/flow increases cost
Equipment running unnecessarily
Leaks in steam and compressed air not detected
Faulty valves or wrong positions → energy loss
Example: 20% air leak → hundreds of millions VND/year in loss

## Slide 8: IMPORTANCE OF MAINTENANCE
Without proper maintenance:
Reduced efficiency, increased energy consumption
Higher risk of breakdowns and downtime
Proper maintenance helps:
Maintain stable energy performance
Extend equipment lifespan
Reduce repair costs, improve safety

## Slide 9: IMPORTANCE OF MAINTENANCE
WELL MAINTAINED EQUIPMENT
POORLY MAINTAINED EQUIPMENT
High Performance
High Reliability
Long Life
Low Performance
Frequent Breakdowns
Unstable Operation

## Slide 10: RELEVANT STANDARDS AND GUIDELINES
ISO 50001: Energy management systems - requirements for effective planning of operations
Circular 38/2023/TT-BCT: Regulations on efficient operation for key energy-using facilities
ISO 55000: Asset management - Application in equipment maintenance
ASME/ASHRAE: International standards for the maintenance of steam and refrigeration systems.
Source: http://www.ashrae.org/​
Source: https://www.asme.org/

## Slide 11
PART 2: OPERATION OF MAIN SYSTEMS

## Slide 12: OPERATION OF BOILER AND STEAM DISTRIBUTION SYSTEM
Control steam output pressure and temperature
Ensure boiler feed water quality (TDS, pH, alkalinity)
Inspect safety valves, pressure gauges, and condensate units
Monitor combustion ratio and optimize load distribution

## Slide 13
HEAT BALANCE & OPTIMIZATION IN BOILER SYSTEM
Monitor: fuel calorific value, combustion efficiency, flue gas losses
Calculate heat balance (input-output): fuel, water, steam, exhaust gas
Use Excel tools or measurement software
Example: Boiler efficiency < 80% → need optimization
Maintain stable pressure (+-0.2 bar)
Distribute load between multiple boilers to improve efficiency
Apply automatic control (PID valve, inverter for feed pump)

## Slide 14
CHILLER OPERATION
Check condensing and evaporating pressures, temperature difference (ΔT)
Ensure clean heat exchangers (condenser, evaporator)
Monitor COP, EER – cold generation efficiency indicators
Adjust cooling load to match demand (load matching)

## Slide 15
REDUCING LEAKS & OPTIMIZING PRESSURE IN COMPRESSED AIR SYSTEM
Common leak points: joints, bent pipes, faulty valves
Use ultrasonic detection devices
Reducing pressure by 1 bar → saves ~7% energy
Increase air storage (tanks) to stabilize pressure

## Slide 16
LIGHTING AND ELECTRIC MOTOR SYSTEM OPERATION
Lighting:
Replace with LED lights, install light/motion sensors
Motors:
Prevent overload/overheating, lubricate periodically
Use IE3+ motors to improve efficiency
Apply VSD/VFD to adjust power based on load (save 30–50%)

## Slide 17
LOAD MANAGEMENT AND ELECTRICITY LOAD
PROFILE OPTIMIZATION
Avoid exceeding registered power capacity to prevent demand penalty
Avoid operating multiple high-power devices simultaneously
Install monitoring devices for real-time tracking

## Slide 18
DISCUSSION QUESTIONS
Please share a situation that you find the mistake during operation in your work. Please give details what did you act/ do and the results?
What should you communication people to avoid this mistake/ false?

## Slide 19
PART 3: EFFECTIVE MAINTENANCE

## Slide 20
PLANNED PREVENTIVE MAINTENANCE
List all equipment requiring maintenance and prioritize
Define maintenance frequency (hours, days, months, years)
Use PM schedules via Excel or CMMS software
Integrate operational data to flexibly adjust plans

## Slide 21
KEY CHECKPOINTS IN ENERGY SYSTEMS
Steam system: steam traps, leaks, pressure reducing valves, condensate filters
Compressed air: oil filter, safety valves, leaks, tank drainage
Chiller: condensing/evaporating pressures, refrigerant, cooling fan
Pump/fan/motor: bearings, vibration, lubrication, shaft alignment
Lighting: replace broken bulbs, check control sensors

## Slide 22
COMMON ISSUES IN COMPRESSED AIR SYSTEMS
1. Compressed air leak
Gas loss rates can be up to 20–30% if not detected and treated promptly.
Common leak points: joints, valves, flexible pipes, rubber gaskets, cylinders
2. Dust and humidity in the air
Corrosion of terminal pneumatic equipment (valves, cylinders, sensors…)
Reduced transmission efficiency, increased maintenance costs
3. Water accumulation in the system
Corrosive to pipes and equipment
May damage pneumatic actuator

## Slide 23
4. Poor filtration and lubrication
Filter is clogged or not changed on time → reduces air flow, increases compressor head pressure
Dirty oil → heats up the machine, causing fire or reducing compressor life
5. Operating the air compressor outside the optimum performance zone
Excessive idling
Set pressure higher than required
COMMON ISSUES IN COMPRESSED AIR SYSTEMS

## Slide 24
Use an ultrasonic detector or soap
Log the location and extent of leaks.
Priority repair of leaks >5 liters/minute
Class item | Recommended Frequency
Leak test​ gas leak | Weekly
Do clean / install new air filter | 3–6 months
Change lubricant | 2,000–4,000 running hours
Check drive belt | 1–3 months
Check gas tank | 1 time/year
Guard born rig do cool | 3–6 months
Check air dryer, drain water | Row day - week
1. Maintenance periodically according to calendar program
2. Check for gas leaks with equipment
EFFICIENT MAINTENANCE OF COMPRESSED AIR SYSTEMS​

## Slide 25
EFFICIENT MAINTENANCE OF COMPRESSED AIR SYSTEMS​
3. Compressor Maintenance
Clean the cooler, replace oil with correct type
Check the motor and soft starter
Inspect exhaust valve, intake valve, and storage tank
4. Maintenance of Dryer and Filter Systems
Dryer (adsorption/refrigerated): replace desiccant, clean heat exchanger
Low-efficiency filters – pre-filters – activated carbon filters: replace as per schedule
5. Calibration and Monitoring
Install pressure and flow sensors at branch points
Periodically calibrate pressure gauges
Integrate remote monitoring (if available)

## Slide 26
6. Solutions to Improve Maintenance Efficiency
Develop detailed SOP for maintenance procedures
Train dedicated technical personnel
Apply maintenance management software (CMMS)
Analyze electricity and air consumption to provide early warnings
Plan for replacing old, low-efficiency equipment
EFFICIENT MAINTENANCE OF COMPRESSED AIR SYSTEMS​

## Slide 27
EFFICIENT MAINTENANCE OF PUMP, FAN, MOTOR SYSTEMS
1. Electric Motors | 
Issue | Consequence
Dirt buildup, vibration, high temperature | Shorter bearing life, burnt coils
Poor ventilation, dirty fan, blocked air flow | Lower efficiency, higher power loss
Misalignment between motor and load | Bearing damage, vibration, strong noise
Lubricant not suitable or insufficient/excessive | Bearing failure, increased friction
Improper startup | High starting current, shorter motor life
2. Water Pumps / Oil Pumps / Vacuum Pumps | 
Issue | Consequence
Shaft seal, mechanical seal, valve leaks | Pressure drop, energy loss
Blocked suction filter/strainer | Reduced flow, heat buildup, burnt pump
Suction of vapor/air | Impeller cavitation, heat buildup

## Slide 28
3. Industrial Fans (exhaust fans, supply fans, cooling towers) | 
Issue | Consequence
Dust buildup on blades, imbalance | Vibration, blade breakage
Loose or worn belt drive | Pulley wear, belt damage
Over-supply of air volume | Energy loss, excess pressure
No inverter control | Operation at non-optimal pressure/flow
EFFICIENT MAINTENANCE OF PUMP, FAN, MOTOR SYSTEMS

## Slide 29
Key Maintenance Practices:
Category | Proposal cycle
Clean dust, lubricate bearings | 1–3 months
Check current, motor temperature | Weekly
Check for vibration and noise | Monthly
Motor shaft and load balance | 6 months – 1 year
Replace belt, maintain gearbox (if any) | 6–12 months
1. Periodic Inspections​​
2. Installation of Monitoring Sensors
Vibration, temperature, and current sensors → early fault detection
Real-time load current monitoring to optimize operation
Use of maintenance monitoring software (CMMS or EMS)
EFFICIENT MAINTENANCE OF PUMP, FAN, MOTOR SYSTEMS

## Slide 30
Key Maintenance Practices:
3. Lubricate properly
Use specialized grease for high speed bearings
Apply the correct amount, at the correct cycle → avoid burning the bearing or causing residual friction
Periodically check the amount of lubricating oil in the pump/gearbox
4. Alignment and concentricity
Apply laser alignment to precisely align the motor and pump/fan
Ensure shaft concentricity → reduce wear, reduce vibration
5. Applying frequency converter (VSD)
For motors, fans, pumps with variable loads → reduce power consumption
Smooth operation, reducing mechanical damage
6. Check the efficiency rate periodic​
Power measurement pepper actual → calculation​​ effect rate (%)
Compare​ with effect rate determine level → exact identify equipment that needs to be replaced or upgraded grant
EFFICIENT MAINTENANCE OF PUMP, FAN, MOTOR SYSTEMS

## Slide 31
DISCUSSION QUESTIONS
What actions has your company taken to improve the maintenance operations of the above systems?
What tools or solutions are used to support effective maintenance?

## Slide 32
EFFICIENT MAINTENANCE OF CHILLER SYSTEMS
Common Issues in Chiller Systems
1. Dust and Fouling in Heat Exchangers
Fouling of the condenser coil leads to reduced heat dissipation efficiency and increased condensing pressure.
Contamination of the evaporator reduces heat exchange efficiency, resulting in chilled water temperatures that fail to meet specifications.
2. Insufficient or Excess Refrigerant (Cooling Gas)
Refrigerant deficiency causes the chiller to underperform and run continuously, leading to excessive power consumption.
Excess refrigerant can cause overpressure and overheating, potentially damaging the compressor.
3. Compressor Malfunction
Excessive vibration, insufficient lubrication, and improper startup procedures reduce compressor lifespan and increase power consumption.
4. Unsynchronized Operation of Chilled Water and Cooling Water Pumps
Lack of coordination among pumps, chiller, and cooling tower leads to instability in water pressure and flow rates.

## Slide 33
5. Cooling tower is dirty, fan is weak
Dirty fan blades, unbalanced → reduced cooling capacity → increased load on the chiller
6. Improper control and load management of the chiller
Chiller runs at 100% even when the load is low → wastes electricity
Lack of synchronization with BMS/EMS systems or inaccurate temperature/pressure sensors
EFFICIENT MAINTENANCE OF CHILLER SYSTEMS

## Slide 34
Category | Recommended Frequency
Clean the heat exchanger (copper tubes, coils) | 3–6 months
Pressure test​ gas pressure , leak rust lip matter cold | Monthly
Check and lubricate bearings and compressor and fan motors | 3 months
Check current, voltage, relay, contactor | 1–3 months
Check expansion valve, temperature sensor | 6 months
BMS calibration/automatic control | 6 months – 1 year
Pump and cooling tower maintenance | 3–6 months
Content of periodic maintenance of chiller system
EFFICIENT MAINTENANCE OF CHILLER SYSTEMS

## Slide 35
Advanced Solutions to Improve Chiller Maintenance
1. Condition-Based Maintenance
Install sensors for current, pressure, and temperature → early detection of anomalies
Monitor COP (Coefficient of Performance) → alerts when efficiency drops
2. Automation and Control
Use Electronic Expansion Valves (EEV) instead of mechanical ones → more accurate and energy-efficient
Install Variable Speed Drives (VSD) for compressors, pumps, and fans → adjust based on cooling load
3. Cold and Cooling Water Management
Maintain water quality: check pH, hardness, and prevent scaling and algae growth
Ensure flow rate and temperature match design capacity
4. Create Operation & Maintenance Logs
Record power consumption, temperature, current, and system faults
Analyze data to develop data-driven maintenance plans
EFFICIENT MAINTENANCE OF CHILLER SYSTEMS

## Slide 36
Key Performance Monitoring Indicators
COP (Cooling Efficiency): If COP < 3, it triggers a maintenance alert.
Chilled Water Supply/Return Temperature: Monitor the ΔT (temperature difference) to assess cooling efficiency.
Chiller Operating Load (%): If the chiller frequently operates below 30% load, the operating strategy should be adjusted.
EFFICIENT MAINTENANCE OF CHILLER SYSTEMS

## Slide 37
DISCUSSION QUESTIONS
What actions has your company taken to improve the maintenance of the chiller system?
What tools or solutions help support effective maintenance?

## Slide 38
EFFICIENT MAINTENANCE OF STEAM SYSTEMS
Common Issues in Steam Systems
1. Steam Leaks
Leaks at flanges, valves, joints, steam traps → significant energy losses (1 leak = tens of millions VND/year)
Condensate leaks affect steam-using equipment
2. Steam Traps Not Operating Efficiently
Faulty traps → loss of live steam or condensate accumulation
Lack of periodic checks → hidden faults go undetected
3. Scaling and Corrosion in Boilers
Scale and sludge in boiler tubes → reduced heat transfer, explosion risk
Corrosion due to low pH or dissolved oxygen → tube damage, shortened boiler life
4. Poor Insulation
Heat loss from pipes, traps, valves, separators → up to 10–20% energy waste
Damaged or unmaintained insulation
5. Poor Steam Pressure and Flow Control
Uncalibrated pressure/safety valves → unstable pressure
Mismatch between supply and demand → steam waste
6. Ineffective Condensate Recovery
Unrecovered condensate → heat, water, and chemical waste
No or improperly designed recovery system

## Slide 39
Maintenance Activities
Item | Recommended Frequency
Clean fire/water tubes | Every 1–3 months
Blowdown, sediment check | Daily
Check for airtightness and smoke leaks | Every 3–6 months
Inspect water supply, pumps, chemicals | Monthly
Check pressure, temperature sensors, relays | Every 3 months
Calibrate safety/pressure valves | Every 6–12 months
1. Boiler​
Item | Recommended Frequency
Inspect insulation | Every 6 months
Check for leaks at joints and valves | Every 3 months
Clean strainers and check valves | Every 3–6 months
2. Piping and Accessories
EFFICIENT MAINTENANCE OF STEAM SYSTEMS

## Slide 40
Maintenance Activities
3. Steam Traps
4. Condensate Recovery and Deaerators
Check deaerator: temperature, pressure, water level
Clean condensate return system, floats, and electric valves
Ensure proper pressure and temperature for reusing recovered condensate
Inspect each trap using ultrasonic devices or temperature checks at inlet/outlet
Replace or repair immediately if leaking or clogged
Maintain diagrams and inspection logs of the entire steam trap system
EFFICIENT MAINTENANCE OF STEAM SYSTEMS

## Slide 41
Solutions to Improve Operation and Maintenance Efficiency
Install steam flow and temperature meters at each branch in use.
Develop a steam system energy diagram ( steam balance )
Automation of water supply, chemicals, pressure control
Conduct regular operator training
Use software to monitor steam consumption by area or product
Indicator | Target
Fuel consumption rate (kg fuel/ton steam) | Decreasing trend over time
Boiler efficiency (%) | >80% (coal), >85% (DO oil), >90% (gas)
Condensate recovery rate (%) | >60%
Steam trap failure rate | <5% across the entire system
Key Performance Indicators
EFFICIENT MAINTENANCE OF STEAM SYSTEMS

## Slide 42
EFFICIENT MAINTENANCE OF LIGHTING SYSTEMS
Common Issues in Lighting Systems
1. Light output degradation over time
Fluorescent, compact, metal halide, and sodium lamps lose 20–40% luminous flux over time
Dusty environments reduce light reflection and overall brightness
2. Flickering or premature lamp failure
Improper installation, unstable voltage, or faulty ballasts (fluorescent lamps)
Faulty drivers in LED lamps
3. Uneven lighting or inadequate illuminance
Poor lamp layout, resulting in dark spots or glare causing eye strain
No regular inspections to adjust or add lighting when needed
4. Manual or non-optimized control
Lights remain on even when daylight is sufficient or area is unoccupied
No zoned lighting control by usage area
5. Lack of maintenance of lamps and reflectors
Dust accumulation reduces lighting efficiency by 10–20%
Reflectors are dirty, broken, or discolored

## Slide 43
Category | Cycle
Clean light bulbs and reflectors | 3–6 months
Check brightness (Lux) with meter | 6 months
Check electrical connections, switches | 6 months
Replace lamp with light loss >30% | When generating electricity
Check driver, ballast, capacitor | 6 months
1. Regular inspection and cleaning
Content of effective maintenance of lighting system
Note each position of the lamp type, capacity, hanging height, and required illuminance.
Bulb replacement, failure, cleaning log → track history for proactive maintenance
2. Create lighting diagrams and inspection logs
EFFICIENT MAINTENANCE OF LIGHTING SYSTEMS

## Slide 44
3. Optimize Control
Install motion sensors in restrooms, storage areas, and low-traffic corridors
Install natural light sensors to automatically adjust lighting levels
Zoned control by area → avoid turning on all lights unnecessarily
4. Upgrade Lighting Equipment
Replace old bulbs (fluorescent, halogen, metal halide...) with high-efficiency LED bulbs (≥130–160 lm/W)
Use LEDs with quality drivers that ensure surge protection and voltage stability
5. Key Monitoring Indicators
Indicator | Target Value
Luminous efficacy (lm/W) | ≥130 for LED; ≥60 for fluorescent
Illuminance at work areas (lux) | 300–750 lux depending on area
Percentage of failed/degraded lamps | <5% across the system
Lighting energy share of total electricity | 10–20% for factories; <30% for office buildings
EFFICIENT MAINTENANCE OF LIGHTING SYSTEMS

## Slide 45
DISCUSSION QUESTIONS
What factors affect the operating efficiency of energy-consuming equipment in your factory?
Which system in your factory most frequently experiences failures due to a lack of maintenance?
If you have a limited budget, which would you prioritize: a) replacing old equipment; b) optimizing operations; or c) investing in monitoring devices? Why?

## Slide 46
THANK YOU